## Changelog
Version | Author | Date | Comments
1 | John Blair | 2013-04-11 | Consolidated 10/12K inverter, Trio inverter, Central module and Ultra Module maps into a single spreadsheet
Removed Common model for Fuse Control Board
2 | John Blair | 2013-04-11 | Formatting improvements
3 | John Blair | 2013-04-17 | Added Communication Board Vendor Model (left out by mistake when I created the consolidated map)
Added Access Mode column (also left out by mistake)
Made Gene's updates to the vendor model
4 | John Blair | 2013-05-21 | Added Serial Number to 64602 (Comm Board)
Added FwVesrsion to both 64602 (Comm Board) and 64603 (Fuse Board)
Added more detail for constant values.
5 | John Blair | 2013-05-21 | Added column for Trio without Comm and Fuse Control Board

## Inverter Modbus
ABB SunSpec Inverter Modbus Map
Start Offset | [11 empty] | Static Contents
block relative | 10/12k | Trio | Trio (No Comm and Fuse Board) | Central (Inverter Module) | Ultra (Inverter Module) | Size | Access Mode | snam | Type | Units | Description | 10/12k | Trio | Central (Inverter Module) | Ultra (Inverter Module) | Comments
sunspec device marker
| 0 | 0 | 0 | 0 | 0 | 2 | R | SID | uint32 | N/A | sunspec id (SunS) | 0x53756e53
common model block (1)
| 2 | 2 | 2 | 2 | 2 | 1 | R | ID | uint16 | N/A | common model id | 1 | 1 | 1 | 1
| 3 | 3 | 3 | 3 | 3 | 1 | R | L | uint16 | Registers | common model length | 66 | 66 | 66 | 66
0 | 4 | 4 | 4 | 4 | 4 | 16 | R | Mn | String(32) | N/A | manufacturer | Power-One (ABB) | Power-One (ABB) | Power-One (ABB) | Power-One (ABB)
16 | 20 | 20 | 20 | 20 | 20 | 16 | R | Md | String(32) | N/A | model |  |  |  |  | <6 digit model string>
32 | 36 | 36 | 36 | 36 | 36 | 8 | R | Opt | String(16) | N/A | options | 4 digit string consisting of AuroraType, GridType, TrafoType and WindType |  |  |  | 4 digit string consisting of AuroraType, GridType, TrafoType and WindType
40 | 44 | 44 | 44 | 44 | 44 | 8 | R | Vr | String(16) | N/A | version |  |  |  |  | inverter firmware version
48 | 52 | 52 | 52 | 52 | 52 | 16 | R | SN | String(32) | N/A | serial number |  |  |  |  | <serial number><model><mfgweek>
64 | 68 | 68 | 68 | 68 | 68 | 1 | R | DA | uint16 | N/A | device address |  |  |  |  | <current modbus address>
65 | 69 | 69 | 69 | 69 | 69 | 1 | R | PAD | PAD | N/A | pad register | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF
three phase inverter model (103)
| 70 | 70 | 70 | 70 | 70 | 1 | R | ID | uint16 |  | three phase inverter model id | 103 | 103 | 103 | 103
| 71 | 71 | 71 | 71 | 71 | 1 | R | L | uint16 |  | three phase inverter model length | 50 | 50 | 50 | 50
0 | 72 | 72 | 72 | 72 | 72 | 1 | R | A | uint16 | A | AC Current
1 | 73 | 73 | 73 | 73 | 73 | 1 | R | AphA | uint16 | A | Phase A Current
2 | 74 | 74 | 74 | 74 | 74 | 1 | R | AphB | uint16 | A | Phase B Current
3 | 75 | 75 | 75 | 75 | 75 | 1 | R | AphC | uint16 | A | Phase C Current
4 | 76 | 76 | 76 | 76 | 76 | 1 | R | A_SF | sunssf |  |  | -2 | -2 | -2 | -2
5 | 77 | 77 | 77 | 77 | 77 | 1 | R | PPVphAB | uint16 | V | Phase Voltage AB | 0x8000 | 0x8000 | 0x8000 | 0x8000 | phase-to-phase voltages not implemented
6 | 78 | 78 | 78 | 78 | 78 | 1 | R | PPVphBC | uint16 | V | Phase Voltage BC | 0x8000 | 0x8000 | 0x8000 | 0x8000
7 | 79 | 79 | 79 | 79 | 79 | 1 | R | PPVphCA | uint16 | V | Phase Voltage CA | 0x8000 | 0x8000 | 0x8000 | 0x8000
8 | 80 | 80 | 80 | 80 | 80 | 1 | R | PhVphA | uint16 | V | Phase Voltage AN
9 | 81 | 81 | 81 | 81 | 81 | 1 | R | PhVphB | uint16 | V | Phase Voltage BN
10 | 82 | 82 | 82 | 82 | 82 | 1 | R | PhVphC | uint16 | V | Phase Voltage CN
11 | 83 | 83 | 83 | 83 | 83 | 1 | R | V_SF | sunssf |  |  | -2 | -2 | -1 | -1 | note differing scale factors
12 | 84 | 84 | 84 | 84 | 84 | 1 | R | W | int16 | W | AC Power
13 | 85 | 85 | 85 | 85 | 85 | 1 | R | W_SF | sunssf |  |  | 0 | 0 | 0 | 0
14 | 86 | 86 | 86 | 86 | 86 | 1 | R | Hz | uint16 | Hz | Line Frequency
15 | 87 | 87 | 87 | 87 | 87 | 1 | R | Hz_SF | sunssf |  |  | -2 | -2 | -2 | -2
16 | 88 | 88 | 88 | 88 | 88 | 1 | R | VA | int16 | VA | AC Apparent Power | 0x8000 | 0x8000 | 0x8000 | 0x8000 | These values should be implemented for larger inverters.
17 | 89 | 89 | 89 | 89 | 89 | 1 | R | VA_SF | sunssf |  |  | 0x8000 | 0x8000 | 0x8000 | 0x8000
18 | 90 | 90 | 90 | 90 | 90 | 1 | R | VAr | int16 | var | AC Reactive Power | 0x8000 | 0x8000 | 0x8000 | 0x8000
19 | 91 | 91 | 91 | 91 | 91 | 1 | R | VAr_SF | sunssf |  |  | 0x8000 | 0x8000 | 0x8000 | 0x8000
20 | 92 | 92 | 92 | 92 | 92 | 1 | R | PF | int16 | Pct | AC Power Factor | 0x8000 | 0x8000 | 0x8000 | 0x8000
21 | 93 | 93 | 93 | 93 | 93 | 1 | R | PF_SF | sunssf |  |  | 0x8000 | 0x8000 | 0x8000 | 0x8000
22 | 94 | 94 | 94 | 94 | 94 | 2 | R | WH | acc32 | Wh | AC Energy
24 | 96 | 96 | 96 | 96 | 96 | 1 | R | WH_SF | sunssf |  |  | 0 | 0 | 0 | 0
25 | 97 | 97 | 97 | 97 | 97 | 1 | R | DCA | uint16 | A | DC Current | 0xFFFF | 0xFFFF |  |  | 10/12K and Trio provide these values in model 160
26 | 98 | 98 | 98 | 98 | 98 | 1 | R | DCA_SF | sunssf |  |  | 0x8000 | 0x8000 | -2 | -2
27 | 99 | 99 | 99 | 99 | 99 | 1 | R | DCV | uint16 | V | DC Voltage | 0xFFFF | 0xFFFF
28 | 100 | 100 | 100 | 100 | 100 | 1 | R | DCV_SF | sunssf |  |  | 0x8000 | 0x8000 | -1 | -1
29 | 101 | 101 | 101 | 101 | 101 | 1 | R | DCW | int16 | W | DC Power
30 | 102 | 102 | 102 | 102 | 102 | 1 | R | DCW_SF | sunssf |  |  | 0 | 0
31 | 103 | 103 | 103 | 103 | 103 | 1 | R | TmpCab | int16 | C | Cabinet Temperature |  |  |  |  | ambient temperature
32 | 104 | 104 | 104 | 104 | 104 | 1 | R | TmpSnk | int16 | C | Heat Sink Temperature | 0x8000 | 0x8000 |  |  | Heatsink temperature on Central
33 | 105 | 105 | 105 | 105 | 105 | 1 | R | TmpTrns | int16 | C | Transformer Temperature | 0x8000 | 0x8000 |  |  | Temperature 2 on central
34 | 106 | 106 | 106 | 106 | 106 | 1 | R | TmpOt | int16 | C | Other Temperature |  |  |  |  | use “booster temperature”
35 | 107 | 107 | 107 | 107 | 107 | 1 | R | Tmp_SF | sunssf |  |  | -1
36 | 108 | 108 | 108 | 108 | 108 | 1 | R | St | enum16 |  | Enumerated value. Operating state |  |  |  |  | See State and Event Detail
37 | 109 | 109 | 109 | 109 | 109 | 1 | R | StVnd | enum16 |  | Vendor specific operating state code |  |  |  |  | Use GlobalSt from vendor model
38 | 110 | 110 | 110 | 110 | 110 | 2 | R | Evt1 | bitfield32 |  | Bitmask value. Event fields |  |  |  |  | See State and Event Detail
40 | 112 | 112 | 112 | 112 | 112 | 2 | R | Evt2 | bitfield32 |  | Reserved for future use | 0 | 0 | 0 | 0
42 | 114 | 114 | 114 | 114 | 114 | 2 | R | EvtVnd1 | bitfield32 |  | Vendor defined events | 0 | 0 | 0 | 0
44 | 116 | 116 | 116 | 116 | 116 | 2 | R | EvtVnd2 | bitfield32 |  | Vendor defined events | 0 | 0 | 0 | 0
46 | 118 | 118 | 118 | 118 | 118 | 2 | R | EvtVnd3 | bitfield32 |  | Vendor defined events | 0 | 0 | 0 | 0
48 | 120 | 120 | 120 | 120 | 120 | 2 | R | EvtVnd4 | bitfield32 |  | Vendor defined events | 0 | 0 | 0 | 0
Multiple MPPT Module Model (ID 160)
| 122 | 122 | 122 |  |  | 1 | R | ID | uint16 |  | Multi-MPPT Module Model ID | 160 | 160 | 160 | 160 | Multiple MPPT Model is not present on Central and Ultra inverter modules
| 123 | 123 | 123 |  |  | 1 | R | L | uint16 |  | Model Length | 48 | 48 | 48 | 48
0 | 124 | 124 | 124 |  |  | 1 | R | DCW_SF | sunssf |  | power scale factor | 0x8000 | 0x8000 | 0x8000 | 0x8000 | unimplemented
1 | 125 | 125 | 125 |  |  | 1 | R | DCA_SF | sunssf |  | current scale factor | -1 | -1 | -1 | -1
2 | 126 | 126 | 126 |  |  | 1 | R | DCV_SF | sunssf |  | voltage scale factor | -1 | -1 | -1 | -1
3 | 127 | 127 | 127 |  |  | 1 | R | DCWH_SF | sunssf |  | energy scale factor | -1 | -1 | -1 | -1
4 | 128 | 128 | 128 |  |  | 2 | R | Evt | bitfield32 |  | event bitfield | See State and Event Detail
6 | 130 | 130 | 130 |  |  | 1 | R | N | uint16 |  | number of DC inputs | 2 | 2 | 2 | 2
7 | 131 | 131 | 131 |  |  | 1 | R | TmsPer | uint16 |  | sampling period | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | unimplemented
Reserved
0 | 132 | 132 | 132 |  |  | 1 | R | ID | uint16 |  | input id | 1 | 1 | 1 | 1
1 | 133 | 133 | 133 |  |  | 8 | R | IDStr | String(16) |  | ID string |  |  |  |  | ID string not used (fill with NULL bytes)
9 | 141 | 141 | 141 |  |  | 1 | R | DCA | uint16 |  | input current
10 | 142 | 142 | 142 |  |  | 1 | R | DCV | uint16 |  | input voltage
11 | 143 | 143 | 143 |  |  | 1 | R | DCW | uint16 |  | input power
12 | 144 | 144 | 144 |  |  | 2 | R | DCWH | acc32 |  | input energy | 0 | 0 | 0 | 0 | unimplemented accumulator
14 | 146 | 146 | 146 |  |  | 2 | R | Tms | uint32 |  | Timestamp | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | unimplemented
16 | 148 | 148 | 148 |  |  | 1 | R | Tmp | int16 |  | temperature | 0x8000 | 0x8000 | 0x8000 | 0x8000 | unimplemented
17 | 149 | 149 | 149 |  |  | 1 | R | DCSt | enum16 |  | operating state | See State and Event Detail
18 | 150 | 150 | 150 |  |  | 2 | R | DCEvt | bitfield32 |  | event bitfield | See State and Event Detail
Reserved
0 | 152 | 152 | 152 |  |  | 1 | R | ID | uint16 |  | input id | 2 | 2 | 2 | 2
1 | 153 | 153 | 153 |  |  | 8 | R | IDStr | String(16) |  | ID string | not used | not used | not used | not used | ID string not used (fill with NULL bytes)
9 | 161 | 161 | 161 |  |  | 1 | R | DCA | uint16 |  | input current
10 | 162 | 162 | 162 |  |  | 1 | R | DCV | uint16 |  | input voltage
11 | 163 | 163 | 163 |  |  | 1 | R | DCW | uint16 |  | input power
12 | 164 | 164 | 164 |  |  | 2 | R | DCWH | acc32 |  | input energy | 0 | 0 | 0 | 0 | unimplemented accumulator
14 | 166 | 166 | 166 |  |  | 2 | R | Tms | uint32 |  | Timestamp | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | unimplemented
16 | 168 | 168 | 168 |  |  | 1 | R | Tmp | int16 |  | temperature | 0x8000 | 0x8000 | 0x8000 | 0x8000 | unimplemented
17 | 169 | 169 | 169 |  |  | 1 | R | DCSt | enum16 |  | operating state | See State and Event Detail
18 | 170 | 170 | 170 |  |  | 2 | R | DCEvt | bitfield32 |  | event bitfield | See State and Event Detail
ABB Inverter Vendor Model (64061)
| 172 | 172 | 172 | 122 | 122 | 1 | R | ID | uint16 | N/A | Uniquely identifies this as the Power-One (ABB) vendor block (registered with SunSpec) | 64061 | 64061 | 64061 | 64061
| 173 | 173 | 173 | 123 | 123 | 1 | R | L | uint16 | Registers | Model length | 124 | 124 | 124 | 124
Status
0 | 174 | 174 | 174 | 124 | 124 | 1 | R | Version | uint16 |  | Future Use: vendor map version number (unimplemented) | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF
1 | 175 | 175 | 175 | 125 | 125 | 4 | R | HwVersion | String(8) |  | Hardware Version String
5 | 179 | 179 | 179 | 129 | 129 | 8 | R | Parent | String(16) |  | Parent String
13 | 187 | 187 | 187 | 137 | 137 | 1 | R | DevicePresence | bitfield16 |  | Bit 0: display present, Bit 1: Comm Board Present, Bit 2: Fuse Control Board Present, Bit 3: Inverter Present (register 174 in current Map
14 | 188 | 188 | 188 | 138 | 138 | 1 | R | GlobalSt | enum16 |  | ABB global state
15 | 189 | 189 | 189 | 139 | 139 | 1 | R | InverterSt | enum16 |  | ABB inverter state
16 | 190 | 190 | 190 | 140 | 140 | 1 | R | DCSt1 | enum16 |  | ABB DC/DC channel 1 state (not mapped)
17 | 191 | 191 | 191 | 141 | 141 | 1 | R | DCSt2 | enum16 |  | ABB DC/DC channel 2 state (not mapped)
18 | 192 | 192 | 192 | 142 | 142 | 2 | RW | SysTime | uint32 |  | System Time (see Aurora Cmd 70)
20 | 194 | 194 | 194 | 144 | 144 | 2 | R | Alarm1 | bitfield32 |  | all possible ABB event codes, arranged in a 256 bit bitfield.
22 | 196 | 196 | 196 | 146 | 146 | 2 | R | Alarm2 | bitfield32
24 | 198 | 198 | 198 | 148 | 148 | 2 | R | Alarm3 | bitfield32
26 | 200 | 200 | 200 | 150 | 150 | 2 | R | Alarm4 | bitfield32 |  | in practice, Alarm4 – Alarm8 are unused
28 | 202 | 202 | 202 | 152 | 152 | 2 | R | Alarm5 | bitfield32
30 | 204 | 204 | 204 | 154 | 154 | 2 | R | Alarm6 | bitfield32
32 | 206 | 206 | 206 | 156 | 156 | 2 | R | Alarm7 | bitfield32
34 | 208 | 208 | 208 | 158 | 158 | 2 | R | Alarm8 | bitfield32
Measurements
36 | 210 | 210 | 210 | 160 | 160 | 2 | R | DayWH | float32 |  | daily production
38 | 212 | 212 | 212 | 162 | 162 | 2 | R | TotalWH | float32 |  | total production
40 | 214 | 214 | 214 | 164 | 164 | 2 | R | PartialWH | float32 |  | partial production (what is this?)
42 | 216 | 216 | 216 | 166 | 166 | 2 | R | WeekWH | float32 |  | week production
44 | 218 | 218 | 218 | 168 | 168 | 2 | R | MonthWH | float32 |  | month production
46 | 220 | 220 | 220 | 170 | 170 | 2 | R | YearWH | float32 |  | year production
48 | 222 | 222 | 222 | 172 | 172 | 2 | R | AC_V | float32 |  | AC voltage
50 | 224 | 224 | 224 | 174 | 174 | 2 | R | AC_A | float32 |  | AC current
52 | 226 | 226 | 226 | 176 | 176 | 2 | R | AC_W | float32 |  | AC power
54 | 228 | 228 | 228 | 178 | 178 | 2 | R | AC_Hz | float32 |  | AC frequency
56 | 230 | 230 | 230 | 180 | 180 | 2 | R | DC1_W | float32 |  | DC input 1 power
58 | 232 | 232 | 232 | 182 | 182 | 2 | R | DC1_V | float32 |  | DC input 1 voltage
60 | 234 | 234 | 234 | 184 | 184 | 2 | R | DC1_A | float32 |  | DC input 1 current
62 | 236 | 236 | 236 | 186 | 186 | 2 | R | DC2_W | float32 |  | DC input 2 power
64 | 238 | 238 | 238 | 188 | 188 | 2 | R | DC2_V | float32 |  | DC input 2 voltage
66 | 240 | 240 | 240 | 190 | 190 | 2 | R | DC2_A | float32 |  | DC input 2 current
68 | 242 | 242 | 242 | 192 | 192 | 2 | R | Tmp | float32 |  | temperature
70 | 244 | 244 | 244 | 194 | 194 | 2 | R | Booster_Tmp | float32 |  | booster temperature
72 | 246 | 246 | 246 | 196 | 196 | 2 | R | Isolation_Ohm1 | float32 |  | isolation resistance, input 1
74 | 248 | 248 | 248 | 198 | 198 | 2 | R | Isolation_Ohm2 | float32 |  | isolation resistance, input 2
76 | 250 | 250 | 250 | 200 | 200 | 2 | R | WindGen_Hz | float32 |  | wind generator frequency
78 | 252 | 252 | 252 | 202 | 202 | 2 | R | Inverter_CosPhi | float32 |  | power factor
80 | 254 | 254 | 254 | 204 | 204 | 1 | R | PAD | pad |  | Reserved for future use
81 | 255 | 255 | 255 | 205 | 205 | 1 | R | PAD | pad |  | Reserved for future use
82 | 256 | 256 | 256 | 206 | 206 | 1 | R | PAD | pad |  | Reserved for future use
83 | 257 | 257 | 257 | 207 | 207 | 1 | R | PAD | pad |  | Reserved for future use
Control
84 | 258 | 258 | 258 | 208 | 208 | 1 | RW | OutputW_Ramp | uint16 | 4s | Power Ramp Rate (range 1 – 250)
85 | 259 | 259 | 259 | 209 | 209 | 1 | RW | OutputW_Timeout | uint16 | minutes | Power Limit Timeout (1 .. 250)
86 | 260 | 260 | 260 | 210 | 210 | 1 | RW | PF_Ramp | uint16 | 4s | Power Factor Ramp Rate (range 1 – 250)
87 | 261 | 261 | 261 | 211 | 211 | 1 | RW | PF_Timeout | uint16 | minutes | Power Factor Timeout (1 .. 250)
88 | 262 | 262 | 262 | 212 | 212 | 1 | R | Remote_Shutdown | enum16 |  | Remote Shut Down Command (write 1 to execute; 0=ON, 1=OFF)
89 | 263 | 263 | 263 | 213 | 213 | 1 | R | PAD | pad |  | Reserved for future use
90 | 264 | 264 | 264 | 214 | 214 | 1 | R | PAD | pad |  | Reserved for future use
91 | 265 | 265 | 265 | 215 | 215 | 1 | R | PAD | pad |  | Reserved for future use
92 | 266 | 266 | 266 | 216 | 216 | 1 | RW | OutputW_Perm | uint16 | % | Output Power (Permanent)
93 | 267 | 267 | 267 | 217 | 217 | 1 | R | OutputW_Perm_St | enum16 |  | Output Power (Permanent) Control Status
94 | 268 | 268 | 268 | 218 | 218 | 2 | RW | PF_Perm | float32 |  | PF adjustment (Permanent)
96 | 270 | 270 | 270 | 220 | 220 | 1 | R | PF_Perm_St | enum16 |  | PF adjustment (Permanent) Control Status
97 | 271 | 271 | 271 | 221 | 221 | 1 | R | PAD | pad |  | Reserved for future use
98 | 272 | 272 | 272 | 222 | 222 | 1 | R | PAD | pad |  | Reserved for future use
99 | 273 | 273 | 273 | 223 | 223 | 1 | R | PAD | pad |  | Reserved for future use
100 | 274 | 274 | 274 | 224 | 224 | 1 | R | PAD | pad |  | Reserved for future use
101 | 275 | 275 | 275 | 225 | 225 | 1 | R | PAD | pad |  | Reserved for future use
102 | 276 | 276 | 276 | 226 | 226 | 1 | RW | OutputW_Dynamic | uint16 | % | Output Power (Dynamic)
103 | 277 | 277 | 277 | 227 | 227 | 1 | R | OutputW_Dynamic_St | enum16 |  | Output Power (Dynamic) Control Status
104 | 278 | 278 | 278 | 228 | 228 | 2 | RW | PF_Dynamic | float32 |  | PF Adjustment (Dynamic)
106 | 280 | 280 | 280 | 230 | 230 | 1 | R | PF_Dynamic_St | enum16 |  | Output Power (Dynamic) Control Status
107 | 281 | 281 | 281 | 231 | 231 | 1 | R | PAD | pad |  | Reserved for future use
108 | 282 | 282 | 282 | 232 | 232 | 1 | R | PAD | pad |  | Reserved for future use
109 | 283 | 283 | 283 | 233 | 233 | 1 | R | PAD | pad |  | Reserved for future use
110 | 284 | 284 | 284 | 234 | 234 | 1 | R | PAD | pad |  | Reserved for future use
111 | 285 | 285 | 285 | 235 | 235 | 1 | R | PAD | pad |  | Reserved for future use
112 | 286 | 286 | 286 | 236 | 236 | 1 | RW | OutputW_Reset | enum16 |  | Write 1 to reset output power to nominal.
113 | 287 | 287 | 287 | 237 | 237 | 1 | R | OutputW_Reset_St | enum16 |  | Output Power Reset Status
114 | 288 | 288 | 288 | 238 | 238 | 1 | RW | PF_Reset | enum16 |  | Write 1 to reset power factor to nominal.
115 | 289 | 289 | 289 | 239 | 239 | 1 | R | PF_Reset_St | enum16 |  | PF Reset Status
Reserved
116 | 290 | 290 | 290 | 240 | 240 | 1 | R | PAD | pad |  | Reserved for future use
117 | 291 | 291 | 291 | 241 | 241 | 1 | R | PAD | pad |  | Reserved for future use
118 | 292 | 292 | 292 | 242 | 242 | 1 | R | PAD | pad |  | Reserved for future use
119 | 293 | 293 | 293 | 243 | 243 | 1 | R | PAD | pad |  | Reserved for future use
120 | 294 | 294 | 294 | 244 | 244 | 1 | R | PAD | pad |  | Reserved for future use
121 | 295 | 295 | 295 | 245 | 245 | 1 | R | PAD | pad |  | Reserved for future use
122 | 296 | 296 | 296 | 246 | 246 | 1 | R | PAD | pad |  | Reserved for future use
123 | 297 | 297 | 297 | 247 | 247 | 1 | R | PAD | pad |  | Reserved for future use
TRIO Communication Board Vendor Block (64062) (TRIO only)
|  | 298 |  |  |  | 1 | R | ID | uint16 | N/A | Uniquely identifies this as the Power -One TRIO vendor block (number to be obtained from Sunspec) | 64062 | 64062 | 64062 | 64062 | Only exists on Trio
|  | 299 |  |  |  | 1 | R | L | uint16 | Registers | Well-known # of 16 bit registers to follow | 36 | 36 | 36 | 36
0 |  | 300 |  |  |  | 8 | R | SN | String(8) |  | Power One Serial Number (model-part#-mfgweek)
8 |  | 308 |  |  |  | 4 | R | FwVersion | String(4) |  | FW version and sub version |  |  |  |  | only uses half of word
12 |  | 312 |  |  |  | 1 | R | St4 | bitfield16 |  | Comm board state byte 4 |  |  |  |  | only uses half of word
13 |  | 313 |  |  |  | 1 | R | St5 | bitfield16 |  | Comm board state byte 5 |  |  |  |  | only uses half of word
14 |  | 314 |  |  |  | 2 | R | PT100 | float32 | C | PT100 sensor
16 |  | 316 |  |  |  | 2 | R | PT1000 | float32 | C | PT1000 sensor
18 |  | 318 |  |  |  | 2 | R | Analog1 | float32 |  | analog input 1
20 |  | 320 |  |  |  | 2 | R | Analog2 | float32 |  | analog input 2
22 |  | 322 |  |  |  | 2 | R | TmpInternal | float32 | C | Internal operating temperature
Analog Input Configuration
24 |  | 324 |  |  |  | 2 | RW | Analog1Gain | float32 |  | Analog 1 gain
26 |  | 326 |  |  |  | 2 | RW | Analog1Offset | float32 |  | Analog 1 offset
28 |  | 328 |  |  |  | 2 | RW | Analog1Units | String(2) |  | Analog 1 units string
30 |  | 330 |  |  |  | 2 | RW | Analog2Gain | float32 |  | Analog 2 gain
32 |  | 332 |  |  |  | 2 | RW | Analog2Offset | float32 |  | Analog 2 offset
34 |  | 334 |  |  |  | 2 | RW | Analog2Units | String(2) |  | Analog 2 units string
Basic String Combiner Model (403) (DC1 Strings, TRIO only)
|  | 336 |  |  |  | 1 | R | ID | unit16 |  | A well-known value 403. Uniquely identifies this as a SunSpec String Combiner (Current) Model |  | 403 |  |  | Only exists on Trio
|  | 337 |  |  |  | 1 | R | L | uint16 |  | Variable # of 16 bit registers to follow : 16+N*8 |  | 56
0 |  | 338 |  |  |  | 1 | R | DCA_SF | sunssf |  | Current scale factor
1 |  | 339 |  |  |  | 1 | R | DCAhr_SF | sunssf |  | Amp-hour scale factor
2 |  | 340 |  |  |  | 1 | R | DCV_SF | sunssf |  | Voltage scale factor
3 |  | 341 |  |  |  | 1 | R | DCAMax | uint16 | A | Maximum DC Current Rating
4 |  | 342 |  |  |  | 1 | R | N | uint16 |  | Number of Inputs
5 |  | 343 |  |  |  | 2 | R | Evt | bitfield32 |  | Bitmask value. Events
7 |  | 345 |  |  |  | 2 | R | EvtVnd | bitfield32 |  | Bitmask value. Vendor defined events
9 |  | 347 |  |  |  | 1 | R | DCA | int16 | A | Total measured current
10 |  | 348 |  |  |  | 2 | R | DCAhr | acc32 | Ah | Total metered Amp-hours
12 |  | 350 |  |  |  | 1 | R | DCV | int16 | V | Output Voltage
13 |  | 351 |  |  |  | 1 | R | Tmp | int16 | C | Internal operating temperature
14 |  | 352 |  |  |  | 1 | R | InDCA_SF | sunssf |  | Current scale factor for inputs
15 |  | 353 |  |  |  | 1 | R | InDCAhr_SF | sunssf |  | Amp-hour scale factor for inputs
Input A |  | Input A
0 |  | 354 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 1
1 |  | 355 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 357 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 359 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 360 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input B |  | Input B
0 |  | 362 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 2
1 |  | 363 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 365 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 367 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 368 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input C |  | Input C
0 |  | 370 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 3
1 |  | 371 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 373 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 375 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 376 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input D |  | Input D
0 |  | 378 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 4
1 |  | 379 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 381 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 383 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 384 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input E |  | Input E
0 |  | 386 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 5
1 |  | 387 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 389 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 391 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 392 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Basic String Combiner Model (403) (DC2 Strings, TRIO only)
|  | 394 |  |  |  | 1 | R | ID | unit16 |  | A well-known value 403. Uniquely identifies this as a SunSpec String Combiner (Current) Model |  | 403 |  |  | Only exists on Trio
|  | 395 |  |  |  | 1 | R | L | uint16 |  | Variable # of 16 bit registers to follow : 16+N*8 |  | 56
0 |  | 396 |  |  |  | 1 | R | DCA_SF | sunssf |  | Current scale factor
1 |  | 397 |  |  |  | 1 | R | DCAhr_SF | sunssf |  | Amp-hour scale factor
2 |  | 398 |  |  |  | 1 | R | DCV_SF | sunssf |  | Voltage scale factor
3 |  | 399 |  |  |  | 1 | R | DCAMax | uint16 | A | Maximum DC Current Rating
4 |  | 400 |  |  |  | 1 | R | N | uint16 |  | Number of Inputs
5 |  | 401 |  |  |  | 2 | R | Evt | bitfield32 |  | Bitmask value. Events
7 |  | 403 |  |  |  | 2 | R | EvtVnd | bitfield32 |  | Bitmask value. Vendor defined events
9 |  | 405 |  |  |  | 1 | R | DCA | int16 | A | Total measured current
10 |  | 406 |  |  |  | 2 | R | DCAhr | acc32 | Ah | Total metered Amp-hours
12 |  | 408 |  |  |  | 1 | R | DCV | int16 | V | Output Voltage
13 |  | 409 |  |  |  | 1 | R | Tmp | int16 | C | Internal operating temperature
14 |  | 410 |  |  |  | 1 | R | InDCA_SF | sunssf |  | Current scale factor for inputs
15 |  | 411 |  |  |  | 1 | R | InDCAhr_SF | sunssf |  | Amp-hour scale factor for inputs
Input A |  | Input A
0 |  | 412 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 1
1 |  | 413 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 415 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 417 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 418 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input B |  | Input B
0 |  | 420 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 2
1 |  | 421 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 423 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 425 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 426 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input C |  | Input C
0 |  | 428 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 3
1 |  | 429 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 431 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 433 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 434 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input D |  | Input D
0 |  | 436 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 4
1 |  | 437 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 439 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 441 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 442 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
Input E |  | Input E
0 |  | 444 |  |  |  | 1 | R | InID | uint16 |  | Uniquely identifies this input set |  | 5
1 |  | 445 |  |  |  | 2 | R | InEvt | bitfield32 |  | String Input Event Flags
3 |  | 447 |  |  |  | 2 | R | InEvtVnd | bitfield32 |  | String Input Vendor Event Flags |  | 0
5 |  | 449 |  |  |  | 1 | R | InDCA | int16 | A | String Input Current
6 |  | 450 |  |  |  | 2 | R | InDCAhr | acc32 | Ah | String Input Amp-Hours |  | 0
TRIO Fuse Control Board Vendor Block (64063)
|  | 452 |  |  |  | 1 | R | ID | uint16 | N/A | Uniquely identifies this as the Power -One TRIO vendor block (number to be obtained from Sunspec) |  | 64063 |  |  | Only exists on Trio
|  | 453 |  |  |  | 1 | R | L | uint16 | Registers | Well-known # of 16 bit registers to follow |  | 18
0 |  | 454 |  |  |  | 8 | R | SN | String(8) |  | Power One Serial Number (model-part#-mfgweek)
8 |  | 462 |  |  |  | 4 | R | FwVersion | String(4) |  | FW version and sub version |  |  |  |  | only uses half of word
12 |  | 466 |  |  |  | 1 | R | St0 | bitfield16 |  | fuse control board state byte 0 |  |  |  |  | only uses half of word
13 |  | 467 |  |  |  | 1 | R | St1 | bitfield16 |  | fuse control board state byte 1 |  |  |  |  | only uses half of word
14 |  | 468 |  |  |  | 1 | R | St2 | bitfield16 |  | fuse control board state byte 2 |  |  |  |  | only uses half of word
15 |  | 469 |  |  |  | 1 | R | St3 | bitfield16 |  | fuse control board state byte 3 |  |  |  |  | only uses half of word
16 |  | 470 |  |  |  | 1 | R | St4 | bitfield16 |  | fuse control board state byte 4 |  |  |  |  | only uses half of word
17 |  | 471 |  |  |  | 1 | R | St5 | bitfield16 |  | fuse control board state byte 5 |  |  |  |  | only uses half of word
End Marker
| 298 | 472 | 298 | 248 | 248 | 1 | R | ID | uint16 |  | SunSpec End Marker | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF
| 299 | 473 | 299 | 249 | 249 | 1 | R | L | uint16 |  | SunSpec End Marker Length | 0 | 0 | 0 | 0

## Status and Events
Mapping Aurora Alarm and State values to Sunspec Status and Event Codes
Vendor Model Bitfield
| Alarm Description | Alarm Code | Sunspec Equivalent | Notes | Point | Bit Number
0 | No Alarm |  |  |  | Alarm1 | 0 | Note that Sunspec requires bit 31 be reserved to assure that 0xFFFFFFFF (not implemented) is not a valid bitfield
1 | Sun Low | W001 |  |  | Alarm1 | 1
2 | Input OC | E001 |  |  | Alarm1 | 2
3 | Input UV | W002 |  |  | Alarm1 | 3
4 | Input OV | E002 | I_EVENT_DC_OVER_VOLT |  | Alarm1 | 4
5 | Sun Low | W001 |  |  | Alarm1 | 5
6 | No Parameters | E003 |  |  | Alarm1 | 6
7 | Bulk OV | E004 |  |  | Alarm1 | 7
8 | Comm. Error | E005 | I_EVENT_MEMORY_LOSS |  | Alarm1 | 8
9 | Output OC | E006 |  |  | Alarm1 | 9
10 | IGBT Sat | E007 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 10
11 | Bulk UV | W011 |  |  | Alarm1 | 11
12 | Internal error | E009 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 12
13 | Grid Fail | W003 | I_EVENT_GRID_DISCONNECT |  | Alarm1 | 13
14 | Bulk Low | E010 |  | what is it? | Alarm1 | 14
15 | Ramp Fail | E011 |  | what is it? | Alarm1 | 15
16 | Dc/Dc Fail | E012 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 16
17 | Wrong Mode | E013 |  | what is it? | Alarm1 | 17
18 | Ground Fault | --- | I_EVENT_GROUND_FAULT |  | Alarm1 | 18
19 | Over Temp. | E014 | I_EVENT_OVER_TEMP |  | Alarm1 | 19
20 | Bulk Cap Fail | E015 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 20
21 | Inverter Fail | E016 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 21
22 | Start Timeout | E017 |  | what is it? | Alarm1 | 22
23 | Ground Fault | E018 | I_EVENT_GROUND_FAULT |  | Alarm1 | 23
24 | AC feed forward | E049 |  |  | Alarm1 | 24
25 | Ileak sens.fail | E019 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 25
26 | DcDc Fail | E012 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 26
27 | Self Test Error 1 | E020 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 27
28 | Self Test Error 2 | E021 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 28
29 | Self Test Error 3 | E019 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 29
30 | Self Test Error 4 | E022 | I_EVENT_HW_TEST_FAILURE |  | Alarm1 | 30
31 | DC inj error | E023 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 0
32 | Grid OV | W004 | I_EVENT_AC_OVER_VOLT |  | Alarm2 | 1
33 | Grid UV | W005 | I_EVENT_AC_UNDER_VOLT |  | Alarm2 | 2
34 | Grid OF | W006 | I_EVENT_OVER_FREQUENCY |  | Alarm2 | 3
35 | Grid UF | W007 | I_EVENT_UNDER_FREQUENCY |  | Alarm2 | 4
36 | Z grid Hi | W008 |  |  | Alarm2 | 5
37 | Internal error | E024 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 6
38 | Riso Low | E025 |  |  | Alarm2 | 7
39 | Vref Error | E026 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 8
40 | Error Meas V | E027 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 9
41 | Error Meas F | E028 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 10
42 | Error Meas Z | E029 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 11
43 | Error Meas Ileak | E030 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 12
44 | Error Read V | E031 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 13
45 | Error Read I | E032 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 14
46 | Table fail | W009 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 15
47 | Fan Fail | W010 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 16
48 | UTH | E033 |  | what is it? | Alarm2 | 17
49 | Interlock fail | E034 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 18
50 | Remote Off | E035 | I_EVENT_MANUAL_SHUTDOWN | ? | Alarm2 | 19
51 | Vout Avg error | E036 |  |  | Alarm2 | 20
52 | Battery low | W012 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 21
53 | Clk fail | W013 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 22
54 | Input UC | E037 |  |  | Alarm2 | 23
55 | Zero Power | W014 |  |  | Alarm2 | 24
56 | Fan Stuck | E038 | I_EVENT_HW_TEST_FAILURE |  | Alarm2 | 25
57 | DC Switch Open | E039 | I_EVENT_DC_DISCONNECT |  | Alarm2 | 26
58 | Tras Switch Open | E040 |  |  | Alarm2 | 27
59 | AC Switch Open | E041 | I_EVENT_AC_DISCONNECT |  | Alarm2 | 28
60 | Bulk UV | E042 |  |  | Alarm2 | 29
61 | Autoexclusion | E043 |  | what is it? | Alarm2 | 30
62 | Grid df/dt | W015 |  |  | Alarm3 | 0
63 | Den switch Open | W016 |  |  | Alarm3 | 1
64 | Jbox fail | W017 | I_EVENT_HW_TEST_FAILURE |  | Alarm3 | 2
65 | DC Door Open | E044 | I_EVENT_CABINET_OPEN |  | Alarm3 | 3
66 | AC Door Open | E045 | I_EVENT_CABINET_OPEN |  | Alarm3 | 4
67 | Anti islanding | --- | I_EVENT_GRID_DISCONNECT |  | Alarm3 | 5
68 | Fuse DC Fail | W020 | I_EVENT_BLOWN_STIRNG_FUSE |  | Alarm3 | 6
69 | Liquid Cooler Fail | E048 | I_EVENT_HW_TEST_FAILURE |  | Alarm3 | 7
70 | SPD AC protection open | W018 |  | what is it? | Alarm3 | 8
71 | SPD DC protection open | W019 |  | what is it? | Alarm3 | 9
72 | String selftest fail | E046 | I_EVENT_HW_TEST_FAILURE |  | Alarm3 | 10
73 | Power reduction start | W021 |  |  | Alarm3 | 11
74 | Power reduction end | W025 |  |  | Alarm3 | 12
75 | React. power mode changed | W022 |  |  | Alarm3 | 13
76 | date/time changed | W023 |  |  | Alarm3 | 14
77 | Energy data reset | W024 |  |  | Alarm3 | 15
State Value | Inverter State Description | Sunspec Equivalent | Notes
0 | Stand By | I_STATUS_STANDBY
1 | Checking Grid | I_STATUS_STARTING
2 | Run | I_STATUS_MPPT
3 | Bulk OV | I_STATUS_FAULT
4 | Out OC | I_STATUS_FAULT
5 | IGBT Sat | I_STATUS_FAULT
6 | Bulk UV | I_STATUS_FAULT
7 | Degauss Error | I_STATUS_FAULT
8 | No Parameters |  | ?
9 | Bulk Low | I_STATUS_FAULT
10 | Grid OV | I_STATUS_FAULT
11 | Communication Error | I_STATUS_FAULT
12 | Degaussing | I_STATUS_STARTING
13 | Starting | I_STATUS_STARTING
14 | Bulk Cap Fail | I_STATUS_FAULT
15 | Leak Fail | I_STATUS_FAULT
16 | DcDc Fail | I_STATUS_FAULT
17 | Ileak Sensor Fail | I_STATUS_FAULT
18 | SelfTest: relay inverter | I_STATUS_STARTING
19 | SelfTest: wait for sensor test | I_STATUS_STARTING
20 | SelfTest: test relay DcDc + sensor | I_STATUS_STARTING
21 | SelfTest: relay inverter fail | I_STATUS_FAULT
22 | SelfTest timeout fail | I_STATUS_FAULT
23 | SelfTest: relay DcDc fail | I_STATUS_FAULT
24 | Self Test 1 | I_STATUS_STARTING
25 | Waiting self test start | I_STATUS_STARTING
26 | Dc Injection |  | ?
27 | Self Test 2 | I_STATUS_STARTING
28 | Self Test 3 | I_STATUS_STARTING
29 | Self Test 4 | I_STATUS_STARTING
30 | Internal Error | I_STATUS_FAULT
31 | Internal Error | I_STATUS_FAULT
40 | Forbidden State | I_STATUS_FAULT
41 | Input UC | I_STATUS_FAULT
42 | Zero Power | I_STATUS_FAULT
43 | Grid Not Present | I_STATUS_FAULT
44 | Waiting Start | I_STATUS_STARTING
45 | MPPT | I_STATUS_MPPT
46 | Grid Fail | I_STATUS_FAULT
47 | Input OC | I_STATUS_FAULT
255 | Inverter Dsp not programmed | I_STATUS_FAULT