## All Points
REST Name (VSN700) | REST Name (VSN300) | SunSpec Normalized Name | HA Entity Name | In /livedata | In /feeds | Label | Description | SunSpec Model | Category | Units | State Class | Device Class | Entity Category | Available in Modbus
Pgrid | m103_1_W | W | abb_m103_w | ✓ | ✓ | Watts | AC Power | M103 | Inverter | W | measurement | power |  | YES
Igrid | m103_1_A | A | abb_m103_a | ✓ |  | Amps | AC Current | M103 | Inverter | A | measurement | current |  | YES
Vgrid | m103_1_PhVphA | PhVphA | abb_m103_phvpha | ✓ |  | Phase Voltage AN | Phase Voltage AN | M103 | Inverter | V | measurement | voltage |  | YES
Fgrid | m103_1_Hz | Hz | abb_m103_hz | ✓ |  | Hz | Line Frequency | M103 | Inverter | Hz | measurement | frequency |  | YES
cosPhi | m103_1_PF | PF | abb_m103_pf | ✓ | ✓ | PF | AC Power Factor | M103 | Inverter | % | measurement | power_factor |  | YES
Qgrid | N/A | VAR | abb_m103_var | ✓ | ✓ | Grid Reactive Power | Grid Reactive Power | M103 | Inverter | var | measurement | reactive_power |  | YES
Pin | m103_1_DCW | DCW | abb_m103_dcw | ✓ | ✓ | DC Watts | DC Power | M103 | Inverter | W | measurement | power |  | YES
ETotal | m103_1_WH | WH | abb_m103_wh | ✓ | ✓ | WattHours | E0 - Inverter Produced Energy - Total | M103 | Inverter | Wh | total_increasing | energy |  | YES
Ein | N/A | Ein | abb_vsn_ein | ✓ | ✓ | Input Energy | Ein - Inverter PV Energy - Total | VSN | Inverter | Wh | total_increasing | energy |  | NO
TempInv | m103_1_TmpOt | TmpOt | abb_m103_tmpot | ✓ |  | Other Temperature | Other Temperature | M103 | Inverter | °C | measurement | temperature |  | YES
Temp1 | m103_1_TmpCab | TmpCab | abb_m103_tmpcab | ✓ | ✓ | Cabinet Temperature | Cabinet Temperature | M103 | Inverter | °C | measurement | temperature |  | YES
WRtg | N/A | WRtg | abb_m120_wrtg | ✓ |  | WRtg | Continuous power output capability of the inverter. | M120 | Inverter | W |  | power |  | YES
Iin1 | m160_1_DCA_1 | DCA_1 | abb_m160_dca_1 | ✓ |  | DC Current #1 | DC Current #1 | M160 | MPPT | A | measurement | current |  | YES
Vin1 | m160_1_DCV_1 | DCV_1 | abb_m160_dcv_1 | ✓ |  | DC Voltage #1 | DC Voltage #1 | M160 | MPPT | V | measurement | voltage |  | YES
Pin1 | m160_1_DCW_1 | DCW_1 | abb_m160_dcw_1 | ✓ | ✓ | DC Power #1 | DC Power #1 | M160 | MPPT | W | measurement | power |  | YES
Iin2 | m160_1_DCA_2 | DCA_2 | abb_m160_dca_2 | ✓ |  | DC Current #2 | DC Current #2 | M160 | MPPT | A | measurement | current |  | YES
Vin2 | m160_1_DCV_2 | DCV_2 | abb_m160_dcv_2 | ✓ |  | DC Voltage #2 | DC Voltage #2 | M160 | MPPT | V | measurement | voltage |  | YES
Pin2 | m160_1_DCW_2 | DCW_2 | abb_m160_dcw_2 | ✓ | ✓ | DC Power #2 | DC Power #2 | M160 | MPPT | W | measurement | power |  | YES
TSoc | N/A | ChaState | abb_m124_chastate | ✓ |  | ChaState | Currently available energy as a percent of the capacity rating. | M124 | Battery | % | measurement | battery |  | YES
PbaT | N/A | InWRte | abb_m124_inwrte | ✓ | ✓ | InWRte | Battery Power - total | M124 | Battery | W | measurement | power |  | YES
Soc | N/A | SoC | abb_m802_soc | ✓ |  | State of Charge | State of charge, expressed as a percentage. | M802 | Battery | % | measurement | battery |  | YES
Soh | N/A | SoH | abb_m802_soh | ✓ |  | State of Health | Percentage of battery life remaining. | M802 | Battery | % | measurement |  |  | YES
Vba | N/A | V | abb_m802_v | ✓ |  | External Battery Voltage | DC Bus Voltage. | M802 | Battery | V | measurement | voltage |  | YES
Iba | N/A | A | abb_m802_a | ✓ |  | Total DC Current | Total DC current flowing to/from the battery bank. | M802 | Battery | A | measurement | current |  | YES
Pba | N/A | W | abb_m802_w | ✓ |  | Total Power | Total power flowing to/from the battery bank. | M802 | Battery | W | measurement | power |  | YES
Tba | N/A | Tmp | abb_m802_tmp | ✓ |  | Battery Temperature | Battery Temperature | M802 | Battery | °C | measurement | temperature |  | YES
CycleNum | N/A | NCyc | abb_m802_ncyc | ✓ |  | Cycle Count | Number of cycles executed in the battery. | M802 | Battery |  | total |  |  | YES
VcMax | N/A | CellVMax | abb_m802_cellvmax | ✓ |  | Max Cell Voltage | Maximum voltage for all cells in the bank. | M802 | Battery | V | measurement | voltage |  | YES
VcMin | N/A | CellVMin | abb_m802_cellvmin | ✓ |  | Min Cell Voltage | Minimum voltage for all cells in the bank. | M802 | Battery | V | measurement | voltage |  | YES
TcMax | N/A | CellTmpMax | abb_m802_celltmpmax | ✓ |  | Tc Max | Tc Max | M802 | Battery | °C | measurement | temperature |  | YES
TcMin | N/A | CellTmpMin | abb_m802_celltmpmin | ✓ |  | Tc Min | Tc Min | M802 | Battery | °C | measurement | temperature |  | YES
PCh | N/A | AChaMax | abb_m802_achamax | ✓ |  | Max Charge Current | Instantaneous maximum DC charge current. | M802 | Battery | A | measurement | current |  | YES
PDh | N/A | ADisChaMax | abb_m802_adischamax | ✓ |  | Max Discharge Current | Instantaneous maximum DC discharge current. | M802 | Battery | A | measurement | current |  | YES
Fcc | N/A | AHRtg | abb_m802_ahrtg | ✓ |  | Nameplate Charge Capacity | Nameplate charge capacity in amp-hours. | M802 | Battery | Ah |  |  |  | YES
VgridL1_N | N/A | PhVphA | abb_m101_phvpha | ✓ |  | Phase Voltage AN | Phase Voltage AN | M101 | Inverter | V | measurement | voltage |  | YES
VgridL2_N | N/A | PhVphB | abb_m101_phvphb | ✓ |  | Phase Voltage BN | Phase Voltage BN | M101 | Inverter | V | measurement | voltage |  | YES
SplitPhase | N/A | SplitPhase | abb_m101_splitphase | ✓ |  | Split Phase | Split Phase | M101 | Inverter |  |  |  |  | YES
MeterPgrid_Tot | N/A | W | abb_m203_w | ✓ | ✓ | Watts | Active Power - total | M203 | Meter | W | measurement | power |  | YES
MeterPgrid_L1 | N/A | WphA | abb_m203_wpha | ✓ |  | Watts phase A | Watts phase A | M203 | Meter | W | measurement | power |  | YES
MeterPgrid_L2 | N/A | WphB | abb_m203_wphb | ✓ |  | Watts phase B | Watts phase B | M203 | Meter | W | measurement | power |  | YES
MeterPgrid_L3 | N/A | WphC | abb_m203_wphc | ✓ |  | Watts phase C | Watts phase C | M203 | Meter | W | measurement | power |  | YES
MeterVgrid_L1 | N/A | PhVphA | abb_m203_phvpha | ✓ |  | Phase Voltage AN | Phase Voltage AN | M203 | Meter | V | measurement | voltage |  | YES
MeterVgrid_L2 | N/A | PhVphB | abb_m203_phvphb | ✓ |  | Phase Voltage BN | Phase Voltage BN | M203 | Meter | V | measurement | voltage |  | YES
MeterVgrid_L3 | N/A | PhVphC | abb_m203_phvphc | ✓ |  | Phase Voltage CN | Phase Voltage CN | M203 | Meter | V | measurement | voltage |  | YES
MeterIgrid_L1 | N/A | AphA | abb_m203_apha | ✓ |  | Amps PhaseA | Phase A Current | M203 | Meter | A | measurement | current |  | YES
MeterIgrid_L2 | N/A | AphB | abb_m203_aphb | ✓ |  | Amps PhaseB | Phase B Current | M203 | Meter | A | measurement | current |  | YES
MeterIgrid_L3 | N/A | AphC | abb_m203_aphc | ✓ |  | Amps PhaseC | Phase C Current | M203 | Meter | A | measurement | current |  | YES
MeterQgrid_Tot | N/A | VAR | abb_m203_var | ✓ |  | VAR | Reactive Power | M203 | Meter | var | measurement | reactive_power |  | YES
MeterQgrid_L1 | N/A | VARphA | abb_m203_varpha | ✓ |  | VAR phase A | VAR phase A | M203 | Meter | var | measurement | reactive_power |  | YES
MeterQgrid_L2 | N/A | VARphB | abb_m203_varphb | ✓ |  | VAR phase B | VAR phase B | M203 | Meter | var | measurement | reactive_power |  | YES
MeterQgrid_L3 | N/A | VARphC | abb_m203_varphc | ✓ |  | VAR phase C | VAR phase C | M203 | Meter | var | measurement | reactive_power |  | YES
MeterFgrid | N/A | Hz | abb_m203_hz | ✓ |  | Hz | Frequency | M203 | Meter | Hz | measurement | frequency |  | YES
EGridImport | N/A | TotWhImp | abb_m203_totwhimp | ✓ | ✓ | Total Watt-hours Imported | E8 - Energy from the Grid - Total | M203 | Meter | Wh | total_increasing | energy |  | YES
EGridExport | N/A | TotWhExp | abb_m203_totwhexp | ✓ | ✓ | Total Watt-hours Exported | E3 - Energy to the Grid - Total | M203 | Meter | Wh | total_increasing | energy |  | YES
E0_1Y | N/A | E0_1Y | abb_m64061_e0_energy_yearly | ✓ | ✓ | E0 Energy Yearly | E0 - Inverter Produced Energy - 1Y | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E0_30D | N/A | E0_30D | abb_m64061_e0_energy_30_day | ✓ | ✓ | E0 Energy 30 Day | E0 - Inverter Produced Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E0_7D | N/A | E0_7D | abb_m64061_e0_energy_7_day | ✓ | ✓ | E0 Energy 7 Day | E0 - Inverter Produced Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E0_runtime | N/A | E0_runtime | abb_m64061_e0_energy_lifetime | ✓ | ✓ | E0 Energy Lifetime | E0 - Inverter Produced Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E15_30D | N/A | E15_30D | abb_m64061_e15_energy_30_day | ✓ | ✓ | E15 Energy 30 Day | E15 - Inverter Backup Output Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E15_7D | N/A | E15_7D | abb_m64061_e15_energy_7_day | ✓ | ✓ | E15 Energy 7 Day | E15 - Inverter Backup Output Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E15_runtime | N/A | E15_runtime | abb_m64061_e15_energy_lifetime | ✓ | ✓ | E15 Energy Lifetime | E15 - Inverter Backup Output Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E1_30D | N/A | E1_30D | abb_m64061_e1_energy_30_day | ✓ | ✓ | E1 Energy 30 Day | E1 - Inverter Absorbed AC Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E1_7D | N/A | E1_7D | abb_m64061_e1_energy_7_day | ✓ | ✓ | E1 Energy 7 Day | E1 - Inverter Absorbed AC Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E1_runtime | N/A | E1_runtime | abb_m64061_e1_energy_lifetime | ✓ | ✓ | E1 Energy Lifetime | E1 - Inverter Absorbed AC Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E2_30D | N/A | E2_30D | abb_m64061_e2_energy_30_day | ✓ | ✓ | E2 Energy 30 Day | E2 - Inverter Apparent AC Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E2_7D | N/A | E2_7D | abb_m64061_e2_energy_7_day | ✓ | ✓ | E2 Energy 7 Day | E2 - Inverter Apparent AC Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E2_runtime | N/A | E2_runtime | abb_m64061_e2_energy_lifetime | ✓ | ✓ | E2 Energy Lifetime | E2 - Inverter Apparent AC Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E3_30D | N/A | E3_30D | abb_m64061_e3_energy_30_day | ✓ | ✓ | E3 Energy 30 Day | E3 - Energy to the Grid - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E3_7D | N/A | E3_7D | abb_m64061_e3_energy_7_day | ✓ | ✓ | E3 Energy 7 Day | E3 - Energy to the Grid - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E3_runtime | N/A | E3_runtime | abb_m64061_e3_energy_lifetime | ✓ | ✓ | E3 Energy Lifetime | E3 - Energy to the Grid - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E4_30D | N/A | E4_30D | abb_m64061_e4_energy_30_day | ✓ |  | E4 Energy 30 Day | E4 Energy 30 Day | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E4_7D | N/A | E4_7D | abb_m64061_e4_energy_7_day | ✓ |  | E4 Energy 7 Day | E4 Energy 7 Day | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E4_runtime | N/A | E4_runtime | abb_m64061_e4_energy_lifetime | ✓ |  | E4 Energy Lifetime | E4 Energy Lifetime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E5_30D | N/A | E5_30D | abb_m64061_e5_energy_30_day | ✓ |  | E5 Energy 30 Day | E5 Energy 30 Day | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E5_7D | N/A | E5_7D | abb_m64061_e5_energy_7_day | ✓ |  | E5 Energy 7 Day | E5 Energy 7 Day | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E5_runtime | N/A | E5_runtime | abb_m64061_e5_energy_lifetime | ✓ |  | E5 Energy Lifetime | E5 Energy Lifetime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E6_30D | N/A | E6_30D | abb_m64061_e6_energy_30_day | ✓ | ✓ | E6 Energy 30 Day | E6 - Consumed Energy from Inverter - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E6_7D | N/A | E6_7D | abb_m64061_e6_energy_7_day | ✓ | ✓ | E6 Energy 7 Day | E6 - Consumed Energy from Inverter - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E6_runtime | N/A | E6_runtime | abb_m64061_e6_energy_lifetime | ✓ | ✓ | E6 Energy Lifetime | E6 - Consumed Energy from Inverter - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E7_30D | N/A | E7_30D | abb_m64061_e7_energy_30_day | ✓ | ✓ | E7 Energy 30 Day | E7 - Consumed Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E7_7D | N/A | E7_7D | abb_m64061_e7_energy_7_day | ✓ | ✓ | E7 Energy 7 Day | E7 - Consumed Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E7_runtime | N/A | E7_runtime | abb_m64061_e7_energy_lifetime | ✓ | ✓ | E7 Energy Lifetime | E7 - Consumed Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E8_30D | N/A | E8_30D | abb_m64061_e8_energy_30_day | ✓ | ✓ | E8 Energy 30 Day | E8 - Energy from the Grid - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E8_7D | N/A | E8_7D | abb_m64061_e8_energy_7_day | ✓ | ✓ | E8 Energy 7 Day | E8 - Energy from the Grid - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
E8_runtime | N/A | E8_runtime | abb_m64061_e8_energy_lifetime | ✓ | ✓ | E8 Energy Lifetime | E8 - Energy from the Grid - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ECharge_30D | N/A | ECharge_30D | abb_m64061_echarge_energy_30_day | ✓ | ✓ | ECharge Energy 30 Day | Battery Charge Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ECharge_7D | N/A | ECharge_7D | abb_m64061_echarge_energy_7_day | ✓ | ✓ | ECharge Energy 7 Day | Battery Charge Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ECharge_runtime | N/A | ECharge_runtime | abb_m64061_echarge_energy_lifetime | ✓ | ✓ | ECharge Energy Lifetime | Battery Charge Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
EDischarge_30D | N/A | EDischarge_30D | abb_m64061_edischarge_energy_30_day | ✓ | ✓ | EDischarge Energy 30 Day | Battery Discharge Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
EDischarge_7D | N/A | EDischarge_7D | abb_m64061_edischarge_energy_7_day | ✓ | ✓ | EDischarge Energy 7 Day | Battery Discharge Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
EDischarge_runtime | N/A | EDischarge_runtime | abb_m64061_edischarge_energy_lifetime | ✓ | ✓ | EDischarge Energy Lifetime | Battery Discharge Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ETotCharge_30D | N/A | ETotCharge_30D | abb_m64061_etotcharge_energy_30_day | ✓ | ✓ | ETotCharge Energy 30 Day | Total Battery Charge Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ETotCharge_7D | N/A | ETotCharge_7D | abb_m64061_etotcharge_energy_7_day | ✓ | ✓ | ETotCharge Energy 7 Day | Total Battery Charge Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ETotCharge_runtime | N/A | ETotCharge_runtime | abb_m64061_etotcharge_energy_lifetime | ✓ | ✓ | ETotCharge Energy Lifetime | Total Battery Charge Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ETotDischarge_30D | N/A | ETotDischarge_30D | abb_m64061_etotdischarge_energy_30_day | ✓ | ✓ | ETotDischarge Energy 30 Day | Total Battery Discharge Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ETotDischarge_7D | N/A | ETotDischarge_7D | abb_m64061_etotdischarge_energy_7_day | ✓ | ✓ | ETotDischarge Energy 7 Day | Total Battery Discharge Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
ETotDischarge_runtime | N/A | ETotDischarge_runtime | abb_m64061_etotdischarge_energy_lifetime | ✓ | ✓ | ETotDischarge Energy Lifetime | Total Battery Discharge Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
Ein_30D | N/A | Ein_30D | abb_m64061_ein_energy_30_day | ✓ | ✓ | Ein Energy 30 Day | Ein - Inverter PV Energy - 30D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
Ein_7D | N/A | Ein_7D | abb_m64061_ein_energy_7_day | ✓ | ✓ | Ein Energy 7 Day | Ein - Inverter PV Energy - 7D | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
Ein_runtime | N/A | Ein_runtime | abb_m64061_ein_energy_lifetime | ✓ | ✓ | Ein Energy Lifetime | Ein - Inverter PV Energy - runtime | M64061 | Energy Counter | Wh | total | energy |  | MAYBE
AlarmState | N/A | AlarmState | abb_m64061_alarm_state | ✓ |  | Alarm State | Alarm State | M64061 | Status |  | measurement |  |  | MAYBE
CountryStd | N/A | CountryStd | abb_m64061_country_std | ✓ |  | Country Std | Country Std | M64061 | Diagnostic |  | measurement |  |  | MAYBE
DC1State | N/A | DC1State | abb_m64061_dc_1_state | ✓ |  | DC 1 State | DC 1 State | M64061 | Status |  | measurement |  |  | MAYBE
DC2State | N/A | DC2State | abb_m64061_dc_2_state | ✓ |  | DC 2 State | DC 2 State | M64061 | Status |  | measurement |  |  | MAYBE
GlobState | N/A | GlobState | abb_m64061_glob_state | ✓ |  | Glob State | Glob State | M64061 | Status |  | measurement |  |  | MAYBE
IleakDC | N/A | IleakDC | abb_m64061_ileak_dc | ✓ |  | Ileak DC | Ileak DC | M64061 | Isolation | A | measurement |  |  | MAYBE
IleakInv | N/A | IleakInv | abb_m64061_ileak_inv | ✓ |  | Ileak Inv | Ileak Inv | M64061 | Isolation | A | measurement |  |  | MAYBE
InvState | N/A | InvState | abb_m64061_inv_state | ✓ |  | Inv State | Inv State | M64061 | Status |  | measurement |  |  | MAYBE
Ppeak | N/A | Ppeak | abb_m64061_ppeak | ✓ |  | Ppeak | Ppeak | M64061 | Diagnostic |  | measurement |  |  | MAYBE
Riso | N/A | Riso | abb_m64061_isolation_resistance | ✓ |  | Isolation Resistance | Isolation Resistance | M64061 | Isolation |  | measurement |  |  | MAYBE
SysTime | m64061_1_SysTime | SysTime | abb_m64061_sys_time | ✓ |  | Sys Time | Sys Time | M64061 | Diagnostic |  | measurement |  |  | MAYBE
TempBst | N/A | TempBst | abb_m64061_boost_temperature | ✓ |  | Boost Temperature | Boost Temperature | M64061 | Diagnostic |  | measurement |  |  | MAYBE
VBulk | m64061_1_VBulk | VBulk | abb_m64061_v_bulk | ✓ |  | V Bulk | V Bulk | M64061 | Isolation | V | measurement | voltage |  | MAYBE
VBulkMid | m64061_1_VBulkMid | VBulkMid | abb_m64061_v_bulk_mid | ✓ |  | V Bulk Mid | V Bulk Mid | M64061 | Isolation | V | measurement | voltage |  | MAYBE
Vgnd | m64061_1_VGnd | Vgnd | abb_m64061_vgnd | ✓ |  | Vgnd | Vgnd | M64061 | Isolation | V | measurement | voltage |  | MAYBE
BattExtCtrlEna | N/A | BattExtCtrlEna | abb_vsn_battextctrlena | ✓ |  | Batt Ext Ctrl Ena | Batt Ext Ctrl Ena | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
BattExtCtrlState | N/A | BattExtCtrlState | abb_vsn_battextctrlstate | ✓ |  | Batt Ext Ctrl State | Batt Ext Ctrl State | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
BattNum | N/A | BattNum | abb_vsn_battnum | ✓ |  | Batt Num | Batt Num | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
BatteryMode | N/A | BatteryMode | abb_vsn_batterymode | ✓ |  | Battery Mode | Battery Mode | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
Chc | N/A | Chc | abb_vsn_chc | ✓ |  | Charge Capacity | Charge Capacity | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
ClockState | N/A | ClockState | abb_vsn_clockstate | ✓ |  | Clock State | Clock State | ABB Proprietary | Other |  | measurement |  |  | NO
CommissioningFreeze | N/A | CommissioningFreeze | abb_vsn_commissioningfreeze | ✓ |  | Commissioning Freeze | Commissioning Freeze | ABB Proprietary | Other |  | measurement |  |  | NO
DI0_mode | N/A | DI0_mode | abb_vsn_di0_mode | ✓ |  | Di 0 Mode | Di 0 Mode | ABB Proprietary | Control |  | measurement |  |  | NO
DI1_mode | N/A | DI1_mode | abb_vsn_di1_mode | ✓ |  | Di 1 Mode | Di 1 Mode | ABB Proprietary | Control |  | measurement |  |  | NO
DI_status | N/A | DI_status | abb_vsn_di_status | ✓ |  | Status | Status | ABB Proprietary | Other |  | measurement |  |  | NO
DetectedBatteryNumber | N/A | DetectedBatteryNumber | abb_vsn_detectedbatterynumber | ✓ |  | Detected Battery Number | Detected Battery Number | ABB Proprietary | Other |  | measurement |  |  | NO
Dhc | N/A | Dhc | abb_vsn_dhc | ✓ |  | Discharge Capacity | Discharge Capacity | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
DynamicFeedInCtrl | N/A | DynamicFeedInCtrl | abb_vsn_dynamicfeedinctrl | ✓ |  | Dynamic Feed In Ctrl | Dynamic Feed In Ctrl | ABB Proprietary | Control |  | measurement |  |  | NO
EBackup | N/A | EBackup | abb_vsn_ebackup | ✓ |  | E Backup | E Backup | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
ECharge | N/A | ECharge | abb_vsn_echarge | ✓ |  | E Charge | E Charge | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
ECt | N/A | ECt | abb_vsn_ect | ✓ |  | E Ct | E Ct | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
EDischarge | N/A | EDischarge | abb_vsn_edischarge | ✓ |  | E Discharge | E Discharge | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
EDt | N/A | EDt | abb_vsn_edt | ✓ |  | E Dt | E Dt | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
ETotalAbsorbed | N/A | ETotalAbsorbed | abb_vsn_etotalabsorbed | ✓ |  | E Total Absorbed | E Total Absorbed | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
ETotalApparent | N/A | ETotalApparent | abb_vsn_etotalapparent | ✓ |  | E Total Apparent | E Total Apparent | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
Ein1 | N/A | Ein1 | abb_vsn_ein1 | ✓ |  | Ein 1 | Ein 1 | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
Ein2 | N/A | Ein2 | abb_vsn_ein2 | ✓ |  | Ein 2 | Ein 2 | ABB Proprietary | Energy Counter |  | total_increasing |  |  | NO
EnergyPolicy | N/A | EnergyPolicy | abb_vsn_energypolicy | ✓ |  | Energy Policy | Energy Policy | ABB Proprietary | Battery Ext |  | total_increasing |  |  | NO
FRT_state | N/A | FRT_state | abb_vsn_frt_state | ✓ |  | State | State | ABB Proprietary | Other |  | measurement |  |  | NO
Fan1rpm | N/A | Fan1rpm | abb_vsn_fan1rpm | ✓ |  | Fan 1 RPM | Fan 1 RPM | ABB Proprietary | System Info |  | measurement |  |  | NO
Fan2rpm | N/A | Fan2rpm | abb_vsn_fan2rpm | ✓ |  | Fan 2 RPM | Fan 2 RPM | ABB Proprietary | System Info |  | measurement |  |  | NO
HouseIgrid_L1 | N/A | HouseIgrid_L1 | abb_vsn_houseigrid_l1 | ✓ |  | House Current Grid L 1 | House Current Grid L 1 | ABB Proprietary | House Meter | A | measurement | current |  | NO
HouseIgrid_L2 | N/A | HouseIgrid_L2 | abb_vsn_houseigrid_l2 | ✓ |  | House Current Grid L 2 | House Current Grid L 2 | ABB Proprietary | House Meter | A | measurement | current |  | NO
HouseIgrid_L3 | N/A | HouseIgrid_L3 | abb_vsn_houseigrid_l3 | ✓ |  | House Current Grid L 3 | House Current Grid L 3 | ABB Proprietary | House Meter | A | measurement | current |  | NO
HousePInverter | N/A | HousePInverter | abb_vsn_housepinverter | ✓ | ✓ | House P Inverter | Home PV Power | ABB Proprietary | House Meter |  | measurement |  |  | NO
HousePgrid_L1 | N/A | HousePgrid_L1 | abb_vsn_housepgrid_l1 | ✓ |  | House Power Grid L 1 | House Power Grid L 1 | ABB Proprietary | House Meter | W | measurement | power |  | NO
HousePgrid_L2 | N/A | HousePgrid_L2 | abb_vsn_housepgrid_l2 | ✓ |  | House Power Grid L 2 | House Power Grid L 2 | ABB Proprietary | House Meter | W | measurement | power |  | NO
HousePgrid_L3 | N/A | HousePgrid_L3 | abb_vsn_housepgrid_l3 | ✓ |  | House Power Grid L 3 | House Power Grid L 3 | ABB Proprietary | House Meter | W | measurement | power |  | NO
HousePgrid_Tot | N/A | HousePgrid_Tot | abb_vsn_housepgrid_tot | ✓ | ✓ | House Power Grid Tot | Load Active Power - total | ABB Proprietary | House Meter | W | measurement | power |  | NO
InputMode | N/A | InputMode | abb_vsn_inputmode | ✓ |  | Input Mode | Input Mode | ABB Proprietary | Control |  | measurement |  |  | NO
NumOfMPPT | N/A | NumOfMPPT | abb_vsn_numofmppt | ✓ |  | Num Of MPPT | Num Of MPPT | ABB Proprietary | System Info |  | measurement |  |  | NO
PACDeratingFlags | N/A | PACDeratingFlags | abb_vsn_pacderatingflags | ✓ |  | Pac Derating Flags | Pac Derating Flags | ABB Proprietary | Control |  | measurement |  |  | NO
PacStandAlone | N/A | PacStandAlone | abb_vsn_pacstandalone | ✓ |  | Pac Stand Alone | Pac Stand Alone | ABB Proprietary | Hybrid |  | measurement |  |  | NO
PacTogrid | N/A | PacTogrid | abb_vsn_pactogrid | ✓ |  | Pac Togrid | Pac Togrid | ABB Proprietary | Hybrid | W | measurement | power |  | NO
QACDeratingFlags | N/A | QACDeratingFlags | abb_vsn_qacderatingflags | ✓ |  | Qac Derating Flags | Qac Derating Flags | ABB Proprietary | Control |  | measurement |  |  | NO
SACDeratingFlags | N/A | SACDeratingFlags | abb_vsn_sacderatingflags | ✓ |  | Sac Derating Flags | Sac Derating Flags | ABB Proprietary | Control |  | measurement |  |  | NO
ShU | N/A | ShU | abb_vsn_shu | ✓ |  | Shutdown | Shutdown | ABB Proprietary | Battery Ext |  | measurement |  |  | NO
WarningFlags | N/A | WarningFlags | abb_vsn_warningflags | ✓ |  | Warning Flags | Warning Flags | ABB Proprietary | Control |  | measurement |  |  | NO
gridExtCtrlEna | N/A | gridExtCtrlEna | abb_vsn_gridextctrlena | ✓ |  | Grid Ext Ctrl Ena | Grid Ext Ctrl Ena | ABB Proprietary | Control |  | measurement |  |  | NO
gridExtCtrlState | N/A | gridExtCtrlState | abb_vsn_gridextctrlstate | ✓ |  | Grid Ext Ctrl State | Grid Ext Ctrl State | ABB Proprietary | Control |  | measurement |  |  | NO
m126Mod_Ena | N/A | m126Mod_Ena | abb_vsn_m126mod_ena | ✓ |  | Model 126 Enable | SunSpec Model 126 Enable Flag | ABB Proprietary | Control |  | measurement |  |  | NO
m132Mod_Ena | N/A | m132Mod_Ena | abb_vsn_m132mod_ena | ✓ |  | Model 132 Enable | SunSpec Model 132 Enable Flag | ABB Proprietary | Control |  | measurement |  |  | NO
N/A | C_DA | C_DA | abb_m1_da | ✓ |  | Da | Da | M1 | Device Info | A | measurement | current | diagnostic | YES
N/A | C_Md | C_Md | abb_m1_md | ✓ |  | Md | Md | M1 | Device Info |  | measurement |  | diagnostic | YES
N/A | C_Mn | C_Mn | abb_m1_mn | ✓ |  | Mn | Mn | M1 | Device Info |  | measurement |  | diagnostic | YES
N/A | C_Opt | C_Opt | abb_m1_opt | ✓ |  | Opt | Opt | M1 | Device Info |  | measurement |  | diagnostic | YES
N/A | C_SN | C_SN | abb_m1_sn | ✓ |  | Sn | Sn | M1 | Device Info |  | measurement |  | diagnostic | YES
N/A | C_Vr | C_Vr | abb_m1_vr | ✓ |  | Vr | Vr | M1 | Device Info | V | measurement | voltage | diagnostic | YES
N/A | CountryStd | CountryStd | abb_vsn_country_std | ✓ |  | Country Std | Country Std | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E0_1Y | E0_1Y | abb_vsn_e0_energy_yearly |  | ✓ | E0 Energy Yearly | E0 - Inverter Produced Energy - 1Y | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E0_30D | E0_30D | abb_vsn_e0_energy_30_day |  | ✓ | E0 Energy 30 Day | E0 - Inverter Produced Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E0_7D | E0_7D | abb_vsn_e0_energy_7_day |  | ✓ | E0 Energy 7 Day | E0 - Inverter Produced Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E0_runtime | E0_runtime | abb_vsn_e0_energy_lifetime |  | ✓ | E0 Energy Lifetime | E0 - Inverter Produced Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E15_30D | E15_30D | abb_vsn_e15_energy_30_day |  | ✓ | E15 Energy 30 Day | E15 - Inverter Backup Output Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E15_7D | E15_7D | abb_vsn_e15_energy_7_day |  | ✓ | E15 Energy 7 Day | E15 - Inverter Backup Output Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E15_runtime | E15_runtime | abb_vsn_e15_energy_lifetime |  | ✓ | E15 Energy Lifetime | E15 - Inverter Backup Output Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E1_30D | E1_30D | abb_vsn_e1_energy_30_day |  | ✓ | E1 Energy 30 Day | E1 - Inverter Absorbed AC Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E1_7D | E1_7D | abb_vsn_e1_energy_7_day |  | ✓ | E1 Energy 7 Day | E1 - Inverter Absorbed AC Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E1_runtime | E1_runtime | abb_vsn_e1_energy_lifetime |  | ✓ | E1 Energy Lifetime | E1 - Inverter Absorbed AC Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E2_30D | E2_30D | abb_vsn_e2_energy_30_day |  | ✓ | E2 Energy 30 Day | E2 - Inverter Apparent AC Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E2_7D | E2_7D | abb_vsn_e2_energy_7_day |  | ✓ | E2 Energy 7 Day | E2 - Inverter Apparent AC Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E2_runtime | E2_runtime | abb_vsn_e2_energy_lifetime |  | ✓ | E2 Energy Lifetime | E2 - Inverter Apparent AC Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E3_30D | E3_30D | abb_vsn_e3_energy_30_day |  | ✓ | E3 Energy 30 Day | E3 - Energy to the Grid - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E3_7D | E3_7D | abb_vsn_e3_energy_7_day |  | ✓ | E3 Energy 7 Day | E3 - Energy to the Grid - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E3_runtime | E3_runtime | abb_vsn_e3_energy_lifetime |  | ✓ | E3 Energy Lifetime | E3 - Energy to the Grid - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E6_30D | E6_30D | abb_vsn_e6_energy_30_day |  | ✓ | E6 Energy 30 Day | E6 - Consumed Energy from Inverter - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E6_7D | E6_7D | abb_vsn_e6_energy_7_day |  | ✓ | E6 Energy 7 Day | E6 - Consumed Energy from Inverter - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E6_runtime | E6_runtime | abb_vsn_e6_energy_lifetime |  | ✓ | E6 Energy Lifetime | E6 - Consumed Energy from Inverter - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E6_total | E6_total | abb_vsn_e_6_total |  | ✓ | E 6 Total | E6 - Consumed Energy from Inverter - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E7_30D | E7_30D | abb_vsn_e7_energy_30_day |  | ✓ | E7 Energy 30 Day | E7 - Consumed Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E7_7D | E7_7D | abb_vsn_e7_energy_7_day |  | ✓ | E7 Energy 7 Day | E7 - Consumed Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E7_runtime | E7_runtime | abb_vsn_e7_energy_lifetime |  | ✓ | E7 Energy Lifetime | E7 - Consumed Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E7_total | E7_total | abb_vsn_e_7_total |  | ✓ | E 7 Total | E7 - Consumed Energy - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E8_30D | E8_30D | abb_vsn_e8_energy_30_day |  | ✓ | E8 Energy 30 Day | E8 - Energy from the Grid - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E8_7D | E8_7D | abb_vsn_e8_energy_7_day |  | ✓ | E8 Energy 7 Day | E8 - Energy from the Grid - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | E8_runtime | E8_runtime | abb_vsn_e8_energy_lifetime |  | ✓ | E8 Energy Lifetime | E8 - Energy from the Grid - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ECharge_30D | ECharge_30D | abb_vsn_echarge_energy_30_day |  | ✓ | ECharge Energy 30 Day | Battery Charge Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ECharge_7D | ECharge_7D | abb_vsn_echarge_energy_7_day |  | ✓ | ECharge Energy 7 Day | Battery Charge Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ECharge_runtime | ECharge_runtime | abb_vsn_echarge_energy_lifetime |  | ✓ | ECharge Energy Lifetime | Battery Charge Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | EDischarge_30D | EDischarge_30D | abb_vsn_edischarge_energy_30_day |  | ✓ | EDischarge Energy 30 Day | Battery Discharge Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | EDischarge_7D | EDischarge_7D | abb_vsn_edischarge_energy_7_day |  | ✓ | EDischarge Energy 7 Day | Battery Discharge Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | EDischarge_runtime | EDischarge_runtime | abb_vsn_edischarge_energy_lifetime |  | ✓ | EDischarge Energy Lifetime | Battery Discharge Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | EGridExport | EGridExport | abb_vsn_e_grid_export |  | ✓ | E Grid Export | E3 - Energy to the Grid - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | EGridImport | EGridImport | abb_vsn_e_grid_import |  | ✓ | E Grid Import | E8 - Energy from the Grid - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotCharge | ETotCharge | abb_vsn_e_tot_charge |  | ✓ | E Tot Charge | Total Battery Charge Energy - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotCharge_30D | ETotCharge_30D | abb_vsn_etotcharge_energy_30_day |  | ✓ | ETotCharge Energy 30 Day | Total Battery Charge Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotCharge_7D | ETotCharge_7D | abb_vsn_etotcharge_energy_7_day |  | ✓ | ETotCharge Energy 7 Day | Total Battery Charge Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotCharge_runtime | ETotCharge_runtime | abb_vsn_etotcharge_energy_lifetime |  | ✓ | ETotCharge Energy Lifetime | Total Battery Charge Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotDischarge | ETotDischarge | abb_vsn_e_tot_discharge |  | ✓ | E Tot Discharge | Total Battery Discharge Energy - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotDischarge_30D | ETotDischarge_30D | abb_vsn_etotdischarge_energy_30_day |  | ✓ | ETotDischarge Energy 30 Day | Total Battery Discharge Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotDischarge_7D | ETotDischarge_7D | abb_vsn_etotdischarge_energy_7_day |  | ✓ | ETotDischarge Energy 7 Day | Total Battery Discharge Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotDischarge_runtime | ETotDischarge_runtime | abb_vsn_etotdischarge_energy_lifetime |  | ✓ | ETotDischarge Energy Lifetime | Total Battery Discharge Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | ETotal | ETotal | abb_vsn_e_total |  | ✓ | E Total | E0 - Inverter Produced Energy - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Ein | Ein | abb_vsn_input_energy |  | ✓ | Input Energy | Ein - Inverter PV Energy - Total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Ein_30D | Ein_30D | abb_vsn_ein_energy_30_day |  | ✓ | Ein Energy 30 Day | Ein - Inverter PV Energy - 30D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Ein_7D | Ein_7D | abb_vsn_ein_energy_7_day |  | ✓ | Ein Energy 7 Day | Ein - Inverter PV Energy - 7D | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Ein_runtime | Ein_runtime | abb_vsn_ein_energy_lifetime |  | ✓ | Ein Energy Lifetime | Ein - Inverter PV Energy - runtime | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | HousePInverter | HousePInverter | abb_vsn_house_p_inverter |  | ✓ | House P Inverter | Home PV Power | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | HousePgrid_Tot | HousePgrid_Tot | abb_vsn_house_power_grid_tot |  | ✓ | House Power Grid Tot | Load Active Power - total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | MeterPgrid_Tot | MeterPgrid_Tot | abb_vsn_meter_power_grid_tot |  | ✓ | Meter Power Grid Tot | Active Power - total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | PbaT | PbaT | abb_vsn_pba_t |  | ✓ | Pba T | Battery Power - total | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Pgrid | Pgrid | abb_vsn_grid_power |  | ✓ | Grid Power | Grid Power | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Pin | Pin | abb_vsn_input_power |  | ✓ | Input Power | Input Power | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Pin1 | Pin1 | abb_vsn_pin_1 |  | ✓ | Pin 1 | Pin 1 | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Pin2 | Pin2 | abb_vsn_pin_2 |  | ✓ | Pin 2 | Pin 2 | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Qgrid | Qgrid | abb_vsn_grid_reactive_power |  | ✓ | Grid Reactive Power | Grid Reactive Power | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | Temp1 | Temp1 | abb_vsn_temp_1 |  | ✓ | Temp 1 | Temp 1 | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | cosPhi | cosPhi | abb_vsn_cos_phi |  | ✓ | Cos Phi | Cos Phi | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | flash_free | flash_free | abb_vsn_flash_free | ✓ | ✓ | Flash Free | flash free | VSN300-only | System Monitoring |  | measurement |  | diagnostic | NO
N/A | free_ram | free_ram | abb_vsn_free_ram | ✓ | ✓ | Free Ram | ram free | VSN300-only | System Monitoring |  | measurement |  | diagnostic | NO
N/A | fw_ver | fw_ver | abb_vsn_fw_ver | ✓ | ✓ | Fw Ver | Version | VSN300-only | System Monitoring |  | measurement |  | diagnostic | NO
IoutR | m103_1_AphA | AphA | abb_m103_amps_phasea | ✓ | ✓ | Amps PhaseA | Phase A Current | M103 | Inverter |  | measurement |  |  | YES
IoutS | m103_1_AphB | AphB | abb_m103_amps_phaseb | ✓ | ✓ | Amps PhaseB | Phase B Current | M103 | Inverter | A | measurement | current |  | YES
IoutT | m103_1_AphC | AphC | abb_m103_amps_phasec | ✓ | ✓ | Amps PhaseC | Phase C Current | M103 | Inverter | A | measurement | current |  | YES
N/A | m103_1_HzA | HzA | abb_m103_frequency_phase_a | ✓ |  | Frequency Phase A | Frequency Phase A | M103 | Inverter | A | measurement | current |  | YES
N/A | m103_1_HzB | HzB | abb_m103_frequency_phase_b | ✓ |  | Frequency Phase B | Frequency Phase B | M103 | Inverter | Hz | measurement | frequency |  | YES
N/A | m103_1_HzC | HzC | abb_m103_frequency_phase_c | ✓ |  | Frequency Phase C | Frequency Phase C | M103 | Inverter | Hz | measurement | frequency |  | YES
VoutRS | m103_1_PhVphAB | PhVphAB | abb_m103_phase_voltage_ab | ✓ | ✓ | Phase Voltage AB | Phase Voltage AB | M103 | Inverter | V | measurement | voltage |  | YES
VoutS | m103_1_PhVphB | PhVphB | abb_m103_phase_voltage_bn | ✓ | ✓ | Phase Voltage BN | Phase Voltage BN | M103 | Inverter | V | measurement | voltage |  | YES
VoutST | m103_1_PhVphBC | PhVphBC | abb_m103_phase_voltage_bc | ✓ | ✓ | Phase Voltage BC | Phase Voltage BC | M103 | Inverter | V | measurement | voltage |  | YES
VoutT | m103_1_PhVphC | PhVphC | abb_m103_phase_voltage_cn | ✓ | ✓ | Phase Voltage CN | Phase Voltage CN | M103 | Inverter | V | measurement | voltage |  | YES
VoutTR | m103_1_PhVphCA | PhVphCA | abb_m103_phase_voltage_ca | ✓ | ✓ | Phase Voltage CA | Phase Voltage CA | M103 | Inverter | A | measurement | current |  | YES
N/A | m103_1_PowerPeakAbs | PowerPeakAbs | abb_m103_peak_power_absolute | ✓ | ✓ | Peak Power (Absolute) | Absolute Pout peak | M103 | Inverter | A | measurement | current |  | YES
N/A | m103_1_PowerPeakToday | PowerPeakToday | abb_m103_peak_power_today | ✓ | ✓ | Peak Power Today | Pout Peak of the day | M103 | Inverter |  | measurement |  |  | YES
N/A | m64061_1_AlarmSt | AlarmSt | abb_m64061_alarm_state | ✓ |  | Alarm State | Alarm State | M64061 | Diagnostic | A | measurement | current |  | NO
N/A | m64061_1_Booster_Tmp | Booster_Tmp | abb_m64061_boost_converter_temperature | ✓ | ✓ | Boost Converter Temperature | Booster stage temperature | M64061 | Diagnostic | °C | measurement | temperature |  | NO
Energy today | m64061_1_DayWH | DayWH | abb_m64061_daily_energy | ✓ | ✓ | Daily Energy | Daily Energy | M64061 | Diagnostic | Wh | total_increasing | energy |  | NO
N/A | m64061_1_DcSt1 | DcSt1 | abb_m64061_dc_input_1_state | ✓ |  | DC Input 1 State | DC Input 1 State | M64061 | Diagnostic |  | measurement |  |  | NO
N/A | m64061_1_DcSt2 | DcSt2 | abb_m64061_dc_input_2_state | ✓ |  | DC Input 2 State | DC Input 2 State | M64061 | Diagnostic |  | measurement |  |  | NO
N/A | m64061_1_GlobalSt | GlobalSt | abb_m64061_global_state | ✓ |  | Global State | Global State | M64061 | Diagnostic |  | measurement |  |  | NO
Ileak 1 | m64061_1_ILeakDcAc | ILeakDcAc | abb_m64061_leakage_current_dc_ac | ✓ | ✓ | Leakage Current DC-AC | Leakage Current DC-AC | M64061 | Diagnostic | A | measurement | current |  | NO
Ileak 2 | m64061_1_ILeakDcDc | ILeakDcDc | abb_m64061_leakage_current_dc_dc | ✓ | ✓ | Leakage Current DC-DC | Leakage Current DC-DC | M64061 | Diagnostic |  | measurement |  |  | NO
N/A | m64061_1_InverterSt | InverterSt | abb_m64061_inverter_state | ✓ |  | Inverter State | Inverter State | M64061 | Diagnostic |  | measurement |  |  | NO
Riso | m64061_1_Isolation_Ohm1 | Isolation_Ohm1 | abb_m64061_isolation_resistance | ✓ | ✓ | Isolation Resistance | Isolation Resistance | M64061 | Diagnostic |  | measurement |  |  | NO
N/A | m64061_1_MonthWH | MonthWH | abb_m64061_monthly_energy | ✓ | ✓ | Monthly Energy | Energy current month | M64061 | Diagnostic | Wh | total_increasing | energy |  | NO
N/A | m64061_1_WeekWH | WeekWH | abb_m64061_weekly_energy | ✓ | ✓ | Weekly Energy | Energy current week | M64061 | Diagnostic | Wh | total_increasing | energy |  | NO
N/A | m64061_1_YearWH | YearWH | abb_m64061_yearly_energy | ✓ | ✓ | Yearly Energy | Energy current year | M64061 | Diagnostic | Wh | total_increasing | energy |  | NO
N/A | pn | pn | abb_vsn_pn | ✓ |  | Pn | Pn | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | sn | sn | abb_vsn_sn | ✓ |  | Sn | Sn | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | store_size | store_size | abb_vsn_store_size | ✓ | ✓ | Store Size | flash used | VSN300-only | System Monitoring |  | measurement |  | diagnostic | NO
N/A | sys_load | sys_load | abb_vsn_sys_load | ✓ | ✓ | Sys Load | system load | VSN300-only | System Monitoring |  | measurement |  | diagnostic | NO
N/A | type | type | abb_vsn_type | ✓ |  | Type | Type | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | uptime | uptime | abb_vsn_uptime | ✓ | ✓ | Uptime | uptime | VSN300-only | System Monitoring |  | measurement |  | diagnostic | NO
N/A | wlan0_essid | wlan0_essid | abb_vsn_wlan_0_essid | ✓ |  | Wlan 0 Essid | Wlan 0 Essid | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | wlan0_ipaddr_local | wlan0_ipaddr_local | abb_vsn_wlan_0_ipaddr_local | ✓ |  | Wlan 0 Ipaddr Local | Wlan 0 Ipaddr Local | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | wlan0_link_quality | wlan0_link_quality | abb_vsn_wlan_0_link_quality | ✓ |  | Wlan 0 Link Quality | Wlan 0 Link Quality | VSN300-only | Unknown |  | measurement |  |  | NO
N/A | wlan0_mode | wlan0_mode | abb_vsn_wlan_0_mode | ✓ |  | Wlan 0 Mode | Wlan 0 Mode | VSN300-only | Unknown |  | measurement |  |  | NO
E6_total | N/A | E6_total | abb_vsn_e_6_total |  | ✓ | E 6 Total | E6 - Consumed Energy from Inverter - Total | VSN700-only | Energy Counter | Wh | total_increasing | energy |  | NO
E7_total | N/A | E7_total | abb_vsn_e_7_total |  | ✓ | E 7 Total | E7 - Consumed Energy - Total | VSN700-only | Energy Counter | Wh | total_increasing | energy |  | NO
ETotCharge | N/A | ETotCharge | abb_vsn_e_tot_charge |  | ✓ | E Tot Charge | Total Battery Charge Energy - Total | VSN700-only | Energy Counter | Wh | total_increasing | energy |  | NO
ETotDischarge | N/A | ETotDischarge | abb_vsn_e_tot_discharge |  | ✓ | E Tot Discharge | Total Battery Discharge Energy - Total | VSN700-only | Energy Counter | Wh | total_increasing | energy |  | NO
flash_free | N/A | flash_free | abb_vsn_flash_free |  | ✓ | Flash Free | flash free | VSN700-only | System Monitoring |  | measurement |  | diagnostic | NO
free_ram | N/A | free_ram | abb_vsn_free_ram |  | ✓ | Free Ram | ram free | VSN700-only | System Monitoring |  | measurement |  | diagnostic | NO
fw_ver | N/A | fw_ver | abb_vsn_fw_ver |  | ✓ | Fw Ver | Version | VSN700-only | System Monitoring |  | measurement |  | diagnostic | NO
store_size | N/A | store_size | abb_vsn_store_size |  | ✓ | Store Size | flash used | VSN700-only | System Monitoring |  | measurement |  | diagnostic | NO
sys_load | N/A | sys_load | abb_vsn_sys_load |  | ✓ | Sys Load | system load | VSN700-only | System Monitoring |  | measurement |  | diagnostic | NO
uptime | N/A | uptime | abb_vsn_uptime |  | ✓ | Uptime | uptime | VSN700-only | System Monitoring |  | measurement |  | diagnostic | NO

## Summary
Category | Count
Total Points | 277
Standard SunSpec (Both protocols) | 72
M64061 (Maybe in Modbus) | 74
ABB Proprietary (REST only) | 47
Diagnostic entities | 18
In /livedata | 208
In /feeds | 148
Points with labels from SunSpec | 277
Points with generated labels | 0