## Index
Model | Label | Description
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digital signature over a specified set of data registers
4 | Secure Dataset Read Response | Compute a digital signature over a specified set of data registers
5 | Secure Write Request | Include a digital signature along with the control data
6 | Secure Write Sequential Request | Include a digital signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings
121 | Basic Settings | Inverter Controls Basic Settings
122 | Measurements_Status | Inverter Controls Extended Measurements and Status
123 | Immediate Controls | Immediate Inverter Controls
124 | Storage | Basic Storage Controls
125 | Pricing | Pricing Signal
126 | Static Volt-VAR | Static Volt-VAR Arrays
127 | Freq-Watt Param | Parameterized Frequency-Watt
128 | Dynamic Reactive Current | Dynamic Reactive Current
129 | LVRTD | LVRT Must Disconnect
130 | HVRTD | HVRT Must Disconnect
131 | Watt-PF | Watt-Power Factor
132 | Volt-Watt | Volt-Watt
133 | Basic Scheduling | Basic Scheduling
134 | Freq-Watt Crv | Curve-Based Frequency-Watt
135 | LFRT | Low Frequency Ride-through
136 | HFRT | High Frequency Ride-through
137 | LVRTC | LVRT must remain connected
138 | HVRTC | HVRT must remain connected
139 | LVRTX | LVRT extended curve
140 | HVRTX | HVRT extended curve
141 | LFRTC | LFRT must remain connected
142 | HFRTC | HFRT must remain connected
143 | LFRTX | LFRT extended curve
144 | HFRTX | HFRT extended curve
145 | Extended Settings | Inverter controls extended settings
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase) single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter
212 | split single phase (ABN) meter
213 | wye-connect three phase (abcn) meter
214 | delta-connect three phase (abc) meter
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orientation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorological Model
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner
402 | String Combiner (Advanced) | An advanced string combiner
403 | String Combiner (Current) | A basic string combiner model
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements
501 | Solar Module | A solar module model supporting DC-DC converter
502 | Solar Module | A solar module model supporting DC-DC converter
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers
701 | DER AC Measurement | DER AC measurement model.
702 | DER Capacity | DER capacity model.
703 | Enter Service | Enter service model.
704 | DER AC Controls | DER AC controls model.
705 | DER Volt-Var | DER Volt-Var model.
706 | DER Volt-Watt | DER Volt-Watt model.
707 | DER Trip LV | DER low voltage trip model.
708 | DER Trip HV | DER high voltage trip model.
709 | DER Trip LF | DER low frequency trip model.
710 | DER Trip HF | DER high frequency trip model.
711 | DER Frequency Droop | DER Frequency Droop model.
712 | DER Watt-Var | DER Watt-Var model.
713 | DER Storage Capacity | DER storage capacity.
714 | DER DC Measurement | DER DC measurement.
715 | DERCtl | DER Control
801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
802 | Battery Base Model
803 | Lithium-Ion Battery Bank Model
804 | Lithium-Ion String Model
805 | Lithium-Ion Module Model
806 | Flow Battery Model
807 | Flow Battery String Model
808 | Flow Battery Module Model
809 | Flow Battery Stack Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller
64410 | DC Simulator Control Interface | A generic DC simulator/power supply control interface for DER electrical testing.
64411 | AC Simulator Control Interface | A generic AC simulator/power supply control interface for DER electrical testing.
64412 | DER Cyber Exploitation | Operations that represent a hacked DER device
64413 | PV Curves | Current-Voltage and Power-Voltage Profiles for PV Simulation.
64414 | DER Simulation Controls | Configuration parameters for the DER device simulator.
64415 | CSIP Client Control | CSIP Client Control for Alarms and Error tests

## 1
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | common |  |  | group | [6 empty] | Common | All SunSpec compliant devices must include this as the first model
0 |  | ID | 1 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length |  | IEEE 1547-2018
2 |  | Mn |  |  | string | 16 |  |  |  | M | S | Manufacturer | Manufacturer |  | IEEE 1547-2018
18 |  | Md |  |  | string | 16 |  |  |  | M | S | Model | Model |  | IEEE 1547-2018
34 |  | Opt |  |  | string | 8 |  |  |  |  | S | Options | Options
42 |  | Vr |  |  | string | 8 |  |  |  |  | S | Version | Version |  | IEEE 1547-2018
50 |  | SN |  |  | string | 16 |  |  |  | M | S | Serial Number | Serial Number |  | IEEE 1547-2018
66 |  | DA |  |  | uint16 |  |  |  | RW |  |  | Device Address | Modbus device address | This point is mandatory for all SunSpec RTU devices and, for those devices, they must support values from 1-247.
67 |  | Pad |  |  | pad | [5 empty] | S |  | Force even alignment

## 2
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | aggregator |  |  | group | [6 empty] | Basic Aggregator | Aggregates a collection of models for a given model id
0 |  | ID | 2 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | AID |  |  | uint16 |  |  |  |  | M |  | AID | Aggregated model id
3 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of aggregated models
4 |  | UN |  |  | uint16 |  |  |  |  | M |  | UN | Update Number. Incrementing number each time the mapping is changed. If the number is not changed from the last reading the direct access to a specific offset will result in reading the same logical model as before. Otherwise the entire model must be read to refresh the changes
5 |  | St |  |  | enum16 |  |  |  |  | M |  | Status | Enumerated status code
|  | OFF | 1
|  | ON | 2
|  | FULL | 3
|  | FAULT | 4
6 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Status | Vendor specific status code
7 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event Code | Bitmask event code
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | RESERVED_5 | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMPERATURE | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMPERATURE | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | THEFT_DETECTION | 16
|  | OUTPUT_OVER_CURRENT | 17
|  | OUTPUT_OVER_VOLTAGE | 18
|  | OUTPUT_UNDER_VOLTAGE | 19
|  | TEST_FAILED | 20
9 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event Code | Vendor specific event code
11 |  | Ctl |  |  | enum16 | [6 empty] | Control | Control register for all aggregated devices
|  | NONE | 0
|  | AUTOMATIC | 1
|  | FORCE_OFF | 2
|  | TEST | 3
|  | THROTTLE | 4
12 |  | CtlVnd |  |  | enum32 | [6 empty] | Vendor Control | Vendor control register for all aggregated devices
14 |  | CtlVl |  |  | enum32 | [6 empty] | Control Value | Numerical value used as a parameter to the control

## 3
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_3 |  |  | group | [6 empty] | Secure Dataset Read Request | Request a digital signature over a specified set of data registers
0 |  | ID | 3 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | X |  |  | uint16 |  |  |  | RW | M |  | X | Number of registers being requested | A max of 50 registers are allowed
3 |  | Off1 |  |  | uint16 |  |  |  | RW | M |  | Offset1 | Offset of value to read
4 |  | Off2 |  |  | uint16 |  |  |  | RW | M
5 |  | Off3 |  |  | uint16 |  |  |  | RW | M
6 |  | Off4 |  |  | uint16 |  |  |  | RW | M
7 |  | Off5 |  |  | uint16 |  |  |  | RW | M
8 |  | Off6 |  |  | uint16 |  |  |  | RW | M
9 |  | Off7 |  |  | uint16 |  |  |  | RW | M
10 |  | Off8 |  |  | uint16 |  |  |  | RW | M
11 |  | Off9 |  |  | uint16 |  |  |  | RW | M
12 |  | Off10 |  |  | uint16 |  |  |  | RW | M
13 |  | Off11 |  |  | uint16 |  |  |  | RW | M
14 |  | Off12 |  |  | uint16 |  |  |  | RW | M
15 |  | Off13 |  |  | uint16 |  |  |  | RW | M
16 |  | Off14 |  |  | uint16 |  |  |  | RW | M
17 |  | Off15 |  |  | uint16 |  |  |  | RW | M
18 |  | Off16 |  |  | uint16 |  |  |  | RW | M
19 |  | Off17 |  |  | uint16 |  |  |  | RW | M
20 |  | Off18 |  |  | uint16 |  |  |  | RW | M
21 |  | Off19 |  |  | uint16 |  |  |  | RW | M
22 |  | Off20 |  |  | uint16 |  |  |  | RW | M
23 |  | Off21 |  |  | uint16 |  |  |  | RW | M
24 |  | Off22 |  |  | uint16 |  |  |  | RW | M
25 |  | Off23 |  |  | uint16 |  |  |  | RW | M
26 |  | Off24 |  |  | uint16 |  |  |  | RW | M
27 |  | Off25 |  |  | uint16 |  |  |  | RW | M
28 |  | Off26 |  |  | uint16 |  |  |  | RW | M
29 |  | Off27 |  |  | uint16 |  |  |  | RW | M
30 |  | Off28 |  |  | uint16 |  |  |  | RW | M
31 |  | Off29 |  |  | uint16 |  |  |  | RW | M
32 |  | Off30 |  |  | uint16 |  |  |  | RW | M
33 |  | Off31 |  |  | uint16 |  |  |  | RW | M
34 |  | Off32 |  |  | uint16 |  |  |  | RW | M
35 |  | Off33 |  |  | uint16 |  |  |  | RW | M
36 |  | Off34 |  |  | uint16 |  |  |  | RW | M
37 |  | Off35 |  |  | uint16 |  |  |  | RW | M
38 |  | Off36 |  |  | uint16 |  |  |  | RW | M
39 |  | Off37 |  |  | uint16 |  |  |  | RW | M
40 |  | Off38 |  |  | uint16 |  |  |  | RW | M
41 |  | Off39 |  |  | uint16 |  |  |  | RW | M
42 |  | Off40 |  |  | uint16 |  |  |  | RW | M
43 |  | Off41 |  |  | uint16 |  |  |  | RW | M
44 |  | Off42 |  |  | uint16 |  |  |  | RW | M
45 |  | Off43 |  |  | uint16 |  |  |  | RW | M
46 |  | Off44 |  |  | uint16 |  |  |  | RW | M
47 |  | Off45 |  |  | uint16 |  |  |  | RW | M
48 |  | Off46 |  |  | uint16 |  |  |  | RW | M
49 |  | Off47 |  |  | uint16 |  |  |  | RW | M
50 |  | Off48 |  |  | uint16 |  |  |  | RW | M
51 |  | Off49 |  |  | uint16 |  |  |  | RW | M
52 |  | Off50 |  |  | uint16 |  |  |  | RW | M
53 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
55 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
56 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request | Shall be advanced for each request
57 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Digital Signature ID | User's role id 0-5
58 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
59 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
|  | model_3.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  |  | M |  | DS | Digital Signature

## 4
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_4 |  |  | group | [6 empty] | Secure Dataset Read Response | Compute a digital signature over a specified set of data registers
0 |  | ID | 4 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | RqSeq |  |  | uint16 |  |  |  |  | M |  | Request Sequence | Sequence number from the request
3 |  | Sts |  |  | enum16 |  |  |  |  | M |  | Status | Status of last read operation
|  | SUCCESS | 0
|  | DS | 1
|  | ACL | 2
|  | OFF | 3
4 |  | X |  |  | uint16 |  |  |  |  | M |  | X | Number of values from the request | A max of 50 values are allocated
5 |  | Val1 |  |  | uint16 |  |  |  |  | M |  | Value1 | Copy of value from register Off1. | Unused values shall return 0xFFFF (unimplemented)
6 |  | Val2 |  |  | uint16 |  |  |  |  | M
7 |  | Val3 |  |  | uint16 |  |  |  |  | M
8 |  | Val4 |  |  | uint16 |  |  |  |  | M
9 |  | Val5 |  |  | uint16 |  |  |  |  | M
10 |  | Val6 |  |  | uint16 |  |  |  |  | M
11 |  | Val7 |  |  | uint16 |  |  |  |  | M
12 |  | Val8 |  |  | uint16 |  |  |  |  | M
13 |  | Val9 |  |  | uint16 |  |  |  |  | M
14 |  | Val10 |  |  | uint16 |  |  |  |  | M
15 |  | Val11 |  |  | uint16 |  |  |  |  | M
16 |  | Val12 |  |  | uint16 |  |  |  |  | M
17 |  | Val13 |  |  | uint16 |  |  |  |  | M
18 |  | Val14 |  |  | uint16 |  |  |  |  | M
19 |  | Val15 |  |  | uint16 |  |  |  |  | M
20 |  | Val16 |  |  | uint16 |  |  |  |  | M
21 |  | Val17 |  |  | uint16 |  |  |  |  | M
22 |  | Val18 |  |  | uint16 |  |  |  |  | M
23 |  | Val19 |  |  | uint16 |  |  |  |  | M
24 |  | Val20 |  |  | uint16 |  |  |  |  | M
25 |  | Val21 |  |  | uint16 |  |  |  |  | M
26 |  | Val22 |  |  | uint16 |  |  |  |  | M
27 |  | Val23 |  |  | uint16 |  |  |  |  | M
28 |  | Val24 |  |  | uint16 |  |  |  |  | M
29 |  | Val25 |  |  | uint16 |  |  |  |  | M
30 |  | Val26 |  |  | uint16 |  |  |  |  | M
31 |  | Val27 |  |  | uint16 |  |  |  |  | M
32 |  | Val28 |  |  | uint16 |  |  |  |  | M
33 |  | Val29 |  |  | uint16 |  |  |  |  | M
34 |  | Val30 |  |  | uint16 |  |  |  |  | M
35 |  | Val31 |  |  | uint16 |  |  |  |  | M
36 |  | Val32 |  |  | uint16 |  |  |  |  | M
37 |  | Val33 |  |  | uint16 |  |  |  |  | M
38 |  | Val34 |  |  | uint16 |  |  |  |  | M
39 |  | Val35 |  |  | uint16 |  |  |  |  | M
40 |  | Val36 |  |  | uint16 |  |  |  |  | M
41 |  | Val37 |  |  | uint16 |  |  |  |  | M
42 |  | Val38 |  |  | uint16 |  |  |  |  | M
43 |  | Val39 |  |  | uint16 |  |  |  |  | M
44 |  | Val40 |  |  | uint16 |  |  |  |  | M
45 |  | Val41 |  |  | uint16 |  |  |  |  | M
46 |  | Val42 |  |  | uint16 |  |  |  |  | M
47 |  | Val43 |  |  | uint16 |  |  |  |  | M
48 |  | Val44 |  |  | uint16 |  |  |  |  | M
49 |  | Val45 |  |  | uint16 |  |  |  |  | M
50 |  | Val46 |  |  | uint16 |  |  |  |  | M
51 |  | Val47 |  |  | uint16 |  |  |  |  | M
52 |  | Val48 |  |  | uint16 |  |  |  |  | M
53 |  | Val49 |  |  | uint16 |  |  |  |  | M
54 |  | Val50 |  |  | uint16 |  |  |  |  | M
55 |  | Ts |  |  | uint32 |  |  |  |  | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
57 |  | Ms |  |  | uint16 |  |  |  |  | M |  | Milliseconds | Millisecond counter 0-999
58 |  | Seq |  |  | uint16 |  |  |  |  | M |  | Sequence | Sequence number of response | Shall be advanced for each response
59 |  | Alm |  |  | enum16 |  |  |  |  | M |  | Alarm | Bitmask alarm code
|  | NONE | 0
|  | ALM | 1
60 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
61 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
|  | model_4.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  |  | M |  | DS | Digital Signature

## 5
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_5 |  |  | group | [6 empty] | Secure Write Request | Include a digital signature along with the control data
0 |  | ID | 5 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | X |  |  | uint16 |  |  |  | RW | M |  | X | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated
3 |  | Off1 |  |  | uint16 |  |  |  | RW | M |  | Offset1 | Offset of control register to write value to
4 |  | Val1 |  |  | uint16 |  |  |  | RW | M |  | Value1 | Value to write to control register at offset
5 |  | Off2 |  |  | uint16 |  |  |  | RW | M
6 |  | Val2 |  |  | uint16 |  |  |  | RW | M
7 |  | Off3 |  |  | uint16 |  |  |  | RW | M
8 |  | Val3 |  |  | uint16 |  |  |  | RW | M
9 |  | Off4 |  |  | uint16 |  |  |  | RW | M
10 |  | Val4 |  |  | uint16 |  |  |  | RW | M
11 |  | Off5 |  |  | uint16 |  |  |  | RW | M
12 |  | Val5 |  |  | uint16 |  |  |  | RW | M
13 |  | Off6 |  |  | uint16 |  |  |  | RW | M
14 |  | Val6 |  |  | uint16 |  |  |  | RW | M
15 |  | Off7 |  |  | uint16 |  |  |  | RW | M
16 |  | Val7 |  |  | uint16 |  |  |  | RW | M
17 |  | Off8 |  |  | uint16 |  |  |  | RW | M
18 |  | Val8 |  |  | uint16 |  |  |  | RW | M
19 |  | Off9 |  |  | uint16 |  |  |  | RW | M
20 |  | Val9 |  |  | uint16 |  |  |  | RW | M
21 |  | Off10 |  |  | uint16 |  |  |  | RW | M
22 |  | Val10 |  |  | uint16 |  |  |  | RW | M
23 |  | Off11 |  |  | uint16 |  |  |  | RW | M
24 |  | Val11 |  |  | uint16 |  |  |  | RW | M
25 |  | Off12 |  |  | uint16 |  |  |  | RW | M
26 |  | Val12 |  |  | uint16 |  |  |  | RW | M
27 |  | Off13 |  |  | uint16 |  |  |  | RW | M
28 |  | Val13 |  |  | uint16 |  |  |  | RW | M
29 |  | Off14 |  |  | uint16 |  |  |  | RW | M
30 |  | Val14 |  |  | uint16 |  |  |  | RW | M
31 |  | Off15 |  |  | uint16 |  |  |  | RW | M
32 |  | Val15 |  |  | uint16 |  |  |  | RW | M
33 |  | Off16 |  |  | uint16 |  |  |  | RW | M
34 |  | Val16 |  |  | uint16 |  |  |  | RW | M
35 |  | Off17 |  |  | uint16 |  |  |  | RW | M
36 |  | Val17 |  |  | uint16 |  |  |  | RW | M
37 |  | Off18 |  |  | uint16 |  |  |  | RW | M
38 |  | Val18 |  |  | uint16 |  |  |  | RW | M
39 |  | Off19 |  |  | uint16 |  |  |  | RW | M
40 |  | Val19 |  |  | uint16 |  |  |  | RW | M
41 |  | Off20 |  |  | uint16 |  |  |  | RW | M
42 |  | Val20 |  |  | uint16 |  |  |  | RW | M
43 |  | Off21 |  |  | uint16 |  |  |  | RW | M
44 |  | Val21 |  |  | uint16 |  |  |  | RW | M
45 |  | Off22 |  |  | uint16 |  |  |  | RW | M
46 |  | Val22 |  |  | uint16 |  |  |  | RW | M
47 |  | Off23 |  |  | uint16 |  |  |  | RW | M
48 |  | Val23 |  |  | uint16 |  |  |  | RW | M
49 |  | Off24 |  |  | uint16 |  |  |  | RW | M
50 |  | Val24 |  |  | uint16 |  |  |  | RW | M
51 |  | Off25 |  |  | uint16 |  |  |  | RW | M
52 |  | Val25 |  |  | uint16 |  |  |  | RW | M
53 |  | Off26 |  |  | uint16 |  |  |  | RW | M
54 |  | Val26 |  |  | uint16 |  |  |  | RW | M
55 |  | Off27 |  |  | uint16 |  |  |  | RW | M
56 |  | Val27 |  |  | uint16 |  |  |  | RW | M
57 |  | Off28 |  |  | uint16 |  |  |  | RW | M
58 |  | Val28 |  |  | uint16 |  |  |  | RW | M
59 |  | Off29 |  |  | uint16 |  |  |  | RW | M
60 |  | Val29 |  |  | uint16 |  |  |  | RW | M
61 |  | Off30 |  |  | uint16 |  |  |  | RW | M
62 |  | Val30 |  |  | uint16 |  |  |  | RW | M
63 |  | Off31 |  |  | uint16 |  |  |  | RW | M
64 |  | Val31 |  |  | uint16 |  |  |  | RW | M
65 |  | Off32 |  |  | uint16 |  |  |  | RW | M
66 |  | Val32 |  |  | uint16 |  |  |  | RW | M
67 |  | Off33 |  |  | uint16 |  |  |  | RW | M
68 |  | Val33 |  |  | uint16 |  |  |  | RW | M
69 |  | Off34 |  |  | uint16 |  |  |  | RW | M
70 |  | Val34 |  |  | uint16 |  |  |  | RW | M
71 |  | Off35 |  |  | uint16 |  |  |  | RW | M
72 |  | Val35 |  |  | uint16 |  |  |  | RW | M
73 |  | Off36 |  |  | uint16 |  |  |  | RW | M
74 |  | Val36 |  |  | uint16 |  |  |  | RW | M
75 |  | Off37 |  |  | uint16 |  |  |  | RW | M
76 |  | Val37 |  |  | uint16 |  |  |  | RW | M
77 |  | Off38 |  |  | uint16 |  |  |  | RW | M
78 |  | Val38 |  |  | uint16 |  |  |  | RW | M
79 |  | Off39 |  |  | uint16 |  |  |  | RW | M
80 |  | Val39 |  |  | uint16 |  |  |  | RW | M
81 |  | Off40 |  |  | uint16 |  |  |  | RW | M
82 |  | Val40 |  |  | uint16 |  |  |  | RW | M
83 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
85 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
86 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request | Shall be advanced for each request
87 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
88 |  | Alg |  |  | enum16 |  |  |  | RW | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
89 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
|  | model_5.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  | RW | M |  | DS | Digital Signature

## 6
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_6 |  |  | group | [6 empty] | Secure Write Sequential Request | Include a digital signature along with the control data
0 |  | ID | 6 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | X |  |  | uint16 |  |  |  | RW | M |  | X | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated
3 |  | Off |  |  | uint16 |  |  |  | RW | M |  | Offset | Starting offset for write operation | X values to follow
4 |  | Val1 |  |  | uint16 |  |  |  | RW | M |  | Value1 | Value to write to control register at offset
5 |  | Val2 |  |  | uint16 |  |  |  | RW | M
6 |  | Val3 |  |  | uint16 |  |  |  | RW | M
7 |  | Val4 |  |  | uint16 |  |  |  | RW | M
8 |  | Val5 |  |  | uint16 |  |  |  | RW | M
9 |  | Val6 |  |  | uint16 |  |  |  | RW | M
10 |  | Val7 |  |  | uint16 |  |  |  | RW | M
11 |  | Val8 |  |  | uint16 |  |  |  | RW | M
12 |  | Val9 |  |  | uint16 |  |  |  | RW | M
13 |  | Val10 |  |  | uint16 |  |  |  | RW | M
14 |  | Val11 |  |  | uint16 |  |  |  | RW | M
15 |  | Val12 |  |  | uint16 |  |  |  | RW | M
16 |  | Val13 |  |  | uint16 |  |  |  | RW | M
17 |  | Val14 |  |  | uint16 |  |  |  | RW | M
18 |  | Val15 |  |  | uint16 |  |  |  | RW | M
19 |  | Val16 |  |  | uint16 |  |  |  | RW | M
20 |  | Val17 |  |  | uint16 |  |  |  | RW | M
21 |  | Val18 |  |  | uint16 |  |  |  | RW | M
22 |  | Val19 |  |  | uint16 |  |  |  | RW | M
23 |  | Val20 |  |  | uint16 |  |  |  | RW | M
24 |  | Val21 |  |  | uint16 |  |  |  | RW | M
25 |  | Val22 |  |  | uint16 |  |  |  | RW | M
26 |  | Val23 |  |  | uint16 |  |  |  | RW | M
27 |  | Val24 |  |  | uint16 |  |  |  | RW | M
28 |  | Val25 |  |  | uint16 |  |  |  | RW | M
29 |  | Val26 |  |  | uint16 |  |  |  | RW | M
30 |  | Val27 |  |  | uint16 |  |  |  | RW | M
31 |  | Val28 |  |  | uint16 |  |  |  | RW | M
32 |  | Val29 |  |  | uint16 |  |  |  | RW | M
33 |  | Val30 |  |  | uint16 |  |  |  | RW | M
34 |  | Val31 |  |  | uint16 |  |  |  | RW | M
35 |  | Val32 |  |  | uint16 |  |  |  | RW | M
36 |  | Val33 |  |  | uint16 |  |  |  | RW | M
37 |  | Val34 |  |  | uint16 |  |  |  | RW | M
38 |  | Val35 |  |  | uint16 |  |  |  | RW | M
39 |  | Val36 |  |  | uint16 |  |  |  | RW | M
40 |  | Val37 |  |  | uint16 |  |  |  | RW | M
41 |  | Val38 |  |  | uint16 |  |  |  | RW | M
42 |  | Val39 |  |  | uint16 |  |  |  | RW | M
43 |  | Val40 |  |  | uint16 |  |  |  | RW | M
44 |  | Val41 |  |  | uint16 |  |  |  | RW | M
45 |  | Val42 |  |  | uint16 |  |  |  | RW | M
46 |  | Val43 |  |  | uint16 |  |  |  | RW | M
47 |  | Val44 |  |  | uint16 |  |  |  | RW | M
48 |  | Val45 |  |  | uint16 |  |  |  | RW | M
49 |  | Val46 |  |  | uint16 |  |  |  | RW | M
50 |  | Val47 |  |  | uint16 |  |  |  | RW | M
51 |  | Val48 |  |  | uint16 |  |  |  | RW | M
52 |  | Val49 |  |  | uint16 |  |  |  | RW | M
53 |  | Val50 |  |  | uint16 |  |  |  | RW | M
54 |  | Val51 |  |  | uint16 |  |  |  | RW | M
55 |  | Val52 |  |  | uint16 |  |  |  | RW | M
56 |  | Val53 |  |  | uint16 |  |  |  | RW | M
57 |  | Val54 |  |  | uint16 |  |  |  | RW | M
58 |  | Val55 |  |  | uint16 |  |  |  | RW | M
59 |  | Val56 |  |  | uint16 |  |  |  | RW | M
60 |  | Val57 |  |  | uint16 |  |  |  | RW | M
61 |  | Val58 |  |  | uint16 |  |  |  | RW | M
62 |  | Val59 |  |  | uint16 |  |  |  | RW | M
63 |  | Val60 |  |  | uint16 |  |  |  | RW | M
64 |  | Val61 |  |  | uint16 |  |  |  | RW | M
65 |  | Val62 |  |  | uint16 |  |  |  | RW | M
66 |  | Val63 |  |  | uint16 |  |  |  | RW | M
67 |  | Val64 |  |  | uint16 |  |  |  | RW | M
68 |  | Val65 |  |  | uint16 |  |  |  | RW | M
69 |  | Val66 |  |  | uint16 |  |  |  | RW | M
70 |  | Val67 |  |  | uint16 |  |  |  | RW | M
71 |  | Val68 |  |  | uint16 |  |  |  | RW | M
72 |  | Val69 |  |  | uint16 |  |  |  | RW | M
73 |  | Val70 |  |  | uint16 |  |  |  | RW | M
74 |  | Val71 |  |  | uint16 |  |  |  | RW | M
75 |  | Val72 |  |  | uint16 |  |  |  | RW | M
76 |  | Val73 |  |  | uint16 |  |  |  | RW | M
77 |  | Val74 |  |  | uint16 |  |  |  | RW | M
78 |  | Val75 |  |  | uint16 |  |  |  | RW | M
79 |  | Val76 |  |  | uint16 |  |  |  | RW | M
80 |  | Val77 |  |  | uint16 |  |  |  | RW | M
81 |  | Val78 |  |  | uint16 |  |  |  | RW | M
82 |  | Val79 |  |  | uint16 |  |  |  | RW | M
83 |  | Val80 |  |  | uint16 |  |  |  | RW | M
84 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
86 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
87 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request | Shall be advanced for each request
88 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
89 |  | Rsrvd |  |  | pad |  |  |  | RW | M
90 |  | Alg |  |  | enum16 |  |  |  | RW | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
91 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
|  | model_6.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  | RW | M |  | DS | Digital Signature

## 7
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_7 |  |  | group | [6 empty] | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response
0 |  | ID | 7 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | RqSeq |  |  | uint16 |  |  |  |  | M |  | Request Sequence | Sequence number from the request
3 |  | Sts |  |  | enum16 |  |  |  |  | M |  | Status | Status of last write operation
|  | SUCCESS | 0
|  | DS | 1
|  | ACL | 2
|  | OFF | 3
|  | VAL | 4
4 |  | Ts |  |  | uint32 |  |  |  |  | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
6 |  | Ms |  |  | uint16 |  |  |  |  | M |  | Milliseconds | Millisecond counter 0-999
7 |  | Seq |  |  | uint16 |  |  |  |  | M |  | Sequence | Sequence number of response | Shall be advanced for each response
8 |  | Alm |  |  | enum16 |  |  |  |  | M |  | Alarm | Bitmask alarm code
|  | NONE | 0
|  | ALM | 1
9 |  | Rsrvd |  |  | pad |  |  |  |  | M
10 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
11 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
|  | model_7.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  | RW | M |  | DS | Digital Signature

## 8
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_8 |  |  | group | [6 empty] | Get Device Security Certificate | Security model for PKI
0 |  | ID | 8 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Fmt |  |  | enum16 |  |  |  |  | M |  | Format | X.509 format of the certificate. DER or PEM.
|  | NONE | 0
|  | X509_PEM | 1
|  | X509_DER | 2
3 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers to follow for the certificate
|  | model_8.repeating |  | 0 | group
| 0 | Cert |  |  | uint16 |  |  |  |  | M |  | Cert | X.509 Certificate of the device

## 9
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_9 |  |  | group | [6 empty] | Set Operator Security Certificate | Security model for PKI
0 |  | ID | 9 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | CertUID |  |  | uint16 |  |  |  | RW | M |  | Cert_UID | User ID for this certificate
3 |  | CertRole |  |  | uint16 |  |  |  | RW | M |  | Cert_Role | Role for this certificate
4 |  | Fmt |  |  | enum16 |  |  |  | RW | M |  | Format | Format of this certificate
|  | NONE | 0
|  | X509_PEM | 1
|  | X509_DER | 2
5 |  | Typ |  |  | enum16 |  |  |  | RW | M |  | Type | Type of this certificate
|  | DEV_KEY_PAIR | 0
|  | DEV_SHARED_KEY | 1
|  | OPERATOR_PUB | 2
|  | OPERATOR_SHARED | 3
|  | CA_PUB | 4
6 |  | TotLn |  |  | uint16 |  |  |  | RW | M |  | Total Length | Total Length of the Certificate | In registers, zero padded.
7 |  | FrgLn |  |  | uint16 |  |  |  | RW | M |  | Fragment length | Length of this fragment | Maximum fragment length is 80 registers
8 |  | Frg1 |  |  | uint16 |  |  |  | RW | M |  | Frag1 | First word of this fragment
9 |  | Frg2 |  |  | uint16 |  |  |  | RW | M
10 |  | Frg3 |  |  | uint16 |  |  |  | RW | M
11 |  | Frg4 |  |  | uint16 |  |  |  | RW | M
12 |  | Frg5 |  |  | uint16 |  |  |  | RW | M
13 |  | Frg6 |  |  | uint16 |  |  |  | RW | M
14 |  | Frg7 |  |  | uint16 |  |  |  | RW | M
15 |  | Frg8 |  |  | uint16 |  |  |  | RW | M
16 |  | Frg9 |  |  | uint16 |  |  |  | RW | M
17 |  | Frg10 |  |  | uint16 |  |  |  | RW | M
18 |  | Frg11 |  |  | uint16 |  |  |  | RW | M
19 |  | Frg12 |  |  | uint16 |  |  |  | RW | M
20 |  | Frg13 |  |  | uint16 |  |  |  | RW | M
21 |  | Frg14 |  |  | uint16 |  |  |  | RW | M
22 |  | Frg15 |  |  | uint16 |  |  |  | RW | M
23 |  | Frg16 |  |  | uint16 |  |  |  | RW | M
24 |  | Frg17 |  |  | uint16 |  |  |  | RW | M
25 |  | Frg18 |  |  | uint16 |  |  |  | RW | M
26 |  | Frg19 |  |  | uint16 |  |  |  | RW | M
27 |  | Frg20 |  |  | uint16 |  |  |  | RW | M
28 |  | Frg21 |  |  | uint16 |  |  |  | RW | M
29 |  | Frg22 |  |  | uint16 |  |  |  | RW | M
30 |  | Frg23 |  |  | uint16 |  |  |  | RW | M
31 |  | Frg24 |  |  | uint16 |  |  |  | RW | M
32 |  | Frg25 |  |  | uint16 |  |  |  | RW | M
33 |  | Frg26 |  |  | uint16 |  |  |  | RW | M
34 |  | Frg27 |  |  | uint16 |  |  |  | RW | M
35 |  | Frg28 |  |  | uint16 |  |  |  | RW | M
36 |  | Frg29 |  |  | uint16 |  |  |  | RW | M
37 |  | Frg30 |  |  | uint16 |  |  |  | RW | M
38 |  | Frg31 |  |  | uint16 |  |  |  | RW | M
39 |  | Frg32 |  |  | uint16 |  |  |  | RW | M
40 |  | Frg33 |  |  | uint16 |  |  |  | RW | M
41 |  | Frg34 |  |  | uint16 |  |  |  | RW | M
42 |  | Frg35 |  |  | uint16 |  |  |  | RW | M
43 |  | Frg36 |  |  | uint16 |  |  |  | RW | M
44 |  | Frg37 |  |  | uint16 |  |  |  | RW | M
45 |  | Frg38 |  |  | uint16 |  |  |  | RW | M
46 |  | Frg39 |  |  | uint16 |  |  |  | RW | M
47 |  | Frg40 |  |  | uint16 |  |  |  | RW | M
48 |  | Frg41 |  |  | uint16 |  |  |  | RW | M
49 |  | Frg42 |  |  | uint16 |  |  |  | RW | M
50 |  | Frg43 |  |  | uint16 |  |  |  | RW | M
51 |  | Frg44 |  |  | uint16 |  |  |  | RW | M
52 |  | Frg45 |  |  | uint16 |  |  |  | RW | M
53 |  | Frg46 |  |  | uint16 |  |  |  | RW | M
54 |  | Frg47 |  |  | uint16 |  |  |  | RW | M
55 |  | Frg48 |  |  | uint16 |  |  |  | RW | M
56 |  | Frg49 |  |  | uint16 |  |  |  | RW | M
57 |  | Frg50 |  |  | uint16 |  |  |  | RW | M
58 |  | Frg51 |  |  | uint16 |  |  |  | RW | M
59 |  | Frg52 |  |  | uint16 |  |  |  | RW | M
60 |  | Frg53 |  |  | uint16 |  |  |  | RW | M
61 |  | Frg54 |  |  | uint16 |  |  |  | RW | M
62 |  | Frg55 |  |  | uint16 |  |  |  | RW | M
63 |  | Frg56 |  |  | uint16 |  |  |  | RW | M
64 |  | Frg57 |  |  | uint16 |  |  |  | RW | M
65 |  | Frg58 |  |  | uint16 |  |  |  | RW | M
66 |  | Frg59 |  |  | uint16 |  |  |  | RW | M
67 |  | Frg60 |  |  | uint16 |  |  |  | RW | M
68 |  | Frg61 |  |  | uint16 |  |  |  | RW | M
69 |  | Frg62 |  |  | uint16 |  |  |  | RW | M
70 |  | Frg63 |  |  | uint16 |  |  |  | RW | M
71 |  | Frg64 |  |  | uint16 |  |  |  | RW | M
72 |  | Frg65 |  |  | uint16 |  |  |  | RW | M
73 |  | Frg66 |  |  | uint16 |  |  |  | RW | M
74 |  | Frg67 |  |  | uint16 |  |  |  | RW | M
75 |  | Frg68 |  |  | uint16 |  |  |  | RW | M
76 |  | Frg69 |  |  | uint16 |  |  |  | RW | M
77 |  | Frg70 |  |  | uint16 |  |  |  | RW | M
78 |  | Frg71 |  |  | uint16 |  |  |  | RW | M
79 |  | Frg72 |  |  | uint16 |  |  |  | RW | M
80 |  | Frg73 |  |  | uint16 |  |  |  | RW | M
81 |  | Frg74 |  |  | uint16 |  |  |  | RW | M
82 |  | Frg75 |  |  | uint16 |  |  |  | RW | M
83 |  | Frg78 |  |  | uint16 |  |  |  | RW | M
84 |  | Frg79 |  |  | uint16 |  |  |  | RW | M
85 |  | Frg80 |  |  | uint16 |  |  |  | RW | M |  | Frag80 | Last word of this fragment
86 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
88 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
89 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request | Shall be advanced for each request
90 |  | UID |  |  | uint16 |  |  |  | RW | M |  | UID | User ID for the request signature
91 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
92 |  | Alg |  |  | enum16 |  |  |  | RW | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
93 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers to follow for the certificate
|  | model_9.repeating |  | 0 | group
| 0 | Cert |  |  | uint16 |  |  |  | RW | M

## 10
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_10 |  |  | group | [6 empty] | Communication Interface Header | To be included first for a complete interface description
0 |  | ID | 10 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | St |  |  | enum16 |  |  |  |  | M |  | Interface Status | Overall interface status
|  | DOWN | 0
|  | UP | 1
|  | FAULT | 2
3 |  | Ctl |  |  | uint16 |  |  |  | RW |  |  | Interface Control | Overall interface control (TBD)
4 |  | Typ |  |  | enum16 | [6 empty] | Physical Access Type | Enumerated value. Type of physical media
|  | UNKNOWN | 0
|  | INTERNAL | 1
|  | TWISTED_PAIR | 2
|  | FIBER | 3
|  | WIRELESS | 4
5 |  | Pad |  |  | pad

## 11
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_11 |  |  | group | [6 empty] | Ethernet Link Layer | Include to support a wired ethernet port
0 |  | ID | 11 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Spd |  |  | uint16 |  |  | Mbps |  | M |  | Ethernet Link Speed | Interface speed in Mb/s
3 |  | CfgSt |  |  | bitfield16 |  |  |  |  | M |  | Interface Status Flags | Bitmask values Interface flags.
|  | LINK | 0
|  | FULL_DUPLEX | 1
|  | AUTO_NEG1 | 2
|  | AUTO_NEG2 | 3
|  | AUTO_NEG3 | 4
|  | RESET_REQUIRED | 5
|  | HW_FAULT | 6
4 |  | St |  |  | enum16 |  |  |  |  | M |  | Link State | Enumerated value. State information for this interface
|  | UNKNOWN | 0
|  | ENABLED | 1
|  | DISABLED | 2
|  | TESTING | 3
5 |  | MAC |  |  | eui48 | [6 empty] | MAC | IEEE MAC address of this interface
9 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name (8 chars)
13 |  | Ctl |  |  | bitfield16 |  |  |  | RW |  |  | Control | Control flags
|  | AUTO | 0
|  | FULL_DUPLEX | 1
14 |  | FrcSpd |  |  | uint16 |  |  | Mbps | RW |  |  | Forced Speed | Forced interface speed in Mb/s when AUTO is disabled

## 12
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_12 |  |  | group | [6 empty] | IPv4 | Include to support an IPv4 protocol stack on this interface
0 |  | ID | 12 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | CfgSt |  |  | enum16 |  |  |  |  | M |  | Config Status | Enumerated value. Configuration status
|  | NOT_CONFIGURED | 0
|  | VALID_SETTING | 1
|  | VALID_HW | 2
7 |  | ChgSt |  |  | bitfield16 |  |  |  |  | M |  | Change Status | Bitmask value. A configuration change is pending
|  | PENDING | 0
8 |  | Cap |  |  | bitfield16 |  |  |  |  | M |  | Config Capability | Bitmask value. Identify capable sources of configuration
|  | DHCP | 0
|  | BOOTP | 1
|  | ZEROCONF | 2
|  | DNS | 3
|  | CFG_SETTABLE | 4
|  | HW_CONFIG | 5
|  | NTP_CLIENT | 6
|  | RESET_REQUIRED | 7
9 |  | Cfg |  |  | enum16 |  |  |  | RW | M |  | IPv4 Config | Enumerated value. Configuration method used.
|  | STATIC | 0
|  | DHCP | 1
|  | BOOTP | 2
|  | ZEROCONF | 3
10 |  | Ctl |  |  | enum16 |  |  |  | RW | M |  | Control | Configure use of services
|  | ENABLE_DNS | 0
|  | ENABLE_NTP | 1
11 |  | Addr |  |  | string | 8 |  |  | RW | M |  | IP | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx
19 |  | Msk |  |  | string | 8 |  |  | RW | M |  | Netmask | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx
27 |  | Gw |  |  | string | 8 |  |  | RW |  |  | Gateway | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx
35 |  | DNS1 |  |  | string | 8 |  |  | RW |  |  | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
43 |  | DNS2 |  |  | string | 8 |  |  | RW |  |  | DNS2 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
51 |  | NTP1 |  |  | string | 12 |  |  | RW |  |  | NTP1 | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
63 |  | NTP2 |  |  | string | 12 |  |  | RW |  |  | NTP2 | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
75 |  | DomNam |  |  | string | 12 |  |  | RW |  |  | Domain | Domain name (24 chars max)
87 |  | HostNam |  |  | string | 12 |  |  | RW |  |  | Host Name | Host name (24 chars max)
99 |  | Pad |  |  | pad

## 13
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_13 |  |  | group | [6 empty] | IPv6 | Include to support an IPv6 protocol stack on this interface
0 |  | ID | 13 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | CfgSt |  |  | enum16 |  |  |  |  | M |  | Config Status | Enumerated value. Configuration status
|  | NOT_CONFIGURED | 0
|  | VALID_SETTING | 1
|  | VALID_HW | 2
7 |  | ChgSt |  |  | bitfield16 |  |  |  |  | M |  | Change Status | Bitmask value. A configuration change is pending
|  | PENDING | 0
8 |  | Cap |  |  | bitfield16 |  |  |  |  | M |  | Config Capability | Bitmask value. Identify capable sources of configuration
|  | DHCP | 0
|  | BOOTP | 1
|  | ZEROCONF | 2
|  | DNS | 3
|  | CFG_SETTABLE | 4
|  | HW_CONFIG | 5
|  | NTP_CLIENT | 6
|  | RESET_REQUIRED | 7
9 |  | Cfg |  |  | enum16 |  |  |  | RW | M |  | IPv6 Config | Enumerated value. Configuration method used.
|  | STATIC | 0
|  | DHCP | 1
|  | BOOTP | 2
|  | ZEROCONF | 3
10 |  | Ctl |  |  | enum16 |  |  |  | RW | M |  | Control | Bitmask value. Configure use of services
|  | ENABLE_DNS | 0
|  | ENABLE_NTP | 1
11 |  | Addr |  |  | string | 20 |  |  | RW | M |  | IP | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
31 |  | CIDR |  |  | string | 20 |  |  | RW |  |  | CIDR | Classless Inter-Domain Routing Number
51 |  | Gw |  |  | string | 20 |  |  | RW |  |  | Gateway | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
71 |  | DNS1 |  |  | string | 20 |  |  | RW |  |  | DNS1 | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
91 |  | DNS2 |  |  | string | 20 |  |  | RW |  |  | DNS2 | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
111 |  | NTP1 |  |  | string | 20 |  |  | RW |  |  | NTP1 | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
131 |  | NTP2 |  |  | string | 20 |  |  | RW |  |  | NTP2 | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
151 |  | DomNam |  |  | string | 12 |  |  | RW |  |  | Domain | Domain name (24 chars max)
163 |  | HostNam |  |  | string | 12 |  |  | RW |  |  | Host Name | Host name (24 chars max)
175 |  | Pad |  |  | pad

## 14
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_14 |  |  | group | [6 empty] | Proxy Server | Include this block to allow for a proxy server
0 |  | ID | 14 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | name | Interface name (8 chars)
6 |  | Cap |  |  | bitfield16 |  |  |  | RW | M |  | Capabilities | Bitmask value. Proxy configuration capabilities
|  | NO_PROXY | 0
|  | IPV4_PROXY | 1
|  | IPV6_PROXY | 2
7 |  | Cfg |  |  | enum16 |  |  |  | RW | M |  | Config | Enumerated value. Set proxy address type
8 |  | Typ |  |  | bitfield16 |  |  |  | RW | M |  | Type | Enumerate value. Proxy server type
9 |  | Addr |  |  | string | 20 |  |  | RW | M |  | Address | IPv4 or IPv6 proxy hostname or dotted address (40 chars)
29 |  | Port |  |  | uint16 |  |  |  | RW | M |  | Port | Proxy port number
30 |  | User |  |  | string | 12 |  |  | RW |  |  | Username | Proxy user name
42 |  | Pw |  |  | string | 12 |  |  | RW |  |  | Password | Proxy password

## 15
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_15 |  |  | group | [6 empty] | Interface Counters Model | Interface counters
0 |  | ID | 15 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Clr |  |  | uint16 |  |  |  | RW |  |  | Clear | Write a "1" to clear all counters
3 |  | InCnt |  |  | acc32 | [6 empty] | Input Count | Number of bytes received
5 |  | InUcCnt |  |  | acc32 | [6 empty] | Input Unicast Count | Number of Unicast packets received
7 |  | InNUcCnt |  |  | acc32 | [6 empty] | Input Non-Unicast Count | Number of non-Unicast packets received
9 |  | InDscCnt |  |  | acc32 | [6 empty] | Input Discarded Count | Number of inbound packets received on the interface but discarded
11 |  | InErrCnt |  |  | acc32 | [6 empty] | Input Error Count | Number of inbound packets that contain errors (excluding discards)
13 |  | InUnkCnt |  |  | acc32 | [6 empty] | Input Unknown Count | Number of inbound packets with unknown protocol
15 |  | OutCnt |  |  | acc32 | [6 empty] | Output Count | Total number of bytes transmitted on this interface
17 |  | OutUcCnt |  |  | acc32 | [6 empty] | Output Unicast Count | Number of Unicast packets transmitted
19 |  | OutNUcCnt |  |  | acc32 | [6 empty] | Output Non-Unicast Count | Number of Non-Unicast packets transmitted
21 |  | OutDscCnt |  |  | acc32 | [6 empty] | Output Discarded Count | Number of Discarded output packets
23 |  | OutErrCnt |  |  | acc32 | [6 empty] | Output Error Count | Number of outbound error packets
25 |  | Pad |  |  | pad

## 16
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_16 |  |  | group | [6 empty] | Simple IP Network | Include this model for a simple IPv4 network stack
0 |  | ID | 16 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name. (8 chars)
6 |  | Cfg |  |  | enum16 |  |  |  |  | M |  | Config | Enumerated value. Force IPv4 configuration method
|  | STATIC | 0
|  | DHCP | 1
7 |  | Ctl |  |  | bitfield16 |  |  |  | RW | M |  | Control | Bitmask value Configure use of services
|  | ENABLE_DNS | 0
|  | ENABLE_NTP | 1
8 |  | Addr |  |  | string | 8 |  |  | RW | M |  | Address | IP address
16 |  | Msk |  |  | string | 8 |  |  | RW | M |  | Netmask | Netmask
24 |  | Gw |  |  | string | 8 |  |  | RW |  |  | Gateway | Gateway IP address
32 |  | DNS1 |  |  | string | 8 |  |  | RW |  |  | DNS1 | 32 bit IP address of DNS server
40 |  | DNS2 |  |  | string | 8 |  |  | RW |  |  | DNS2 | 32 bit IP address of DNS server
48 |  | MAC |  |  | eui48 | [6 empty] | MAC | IEEE MAC address of this interface
52 |  | LnkCtl |  |  | bitfield16 |  |  |  | RW |  |  | Link Control | Bitmask value. Link control flags
|  | AUTONEGOTIATE | 0
|  | FULL_DUPLEX | 1
|  | FORCE_10MB | 2
|  | FORCE_100MB | 3
|  | FORCE_1GB | 4
53 |  | Pad |  |  | pad

## 17
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_17 |  |  | group | [6 empty] | Serial Interface | Include this model for serial interface configuration support
0 |  | ID | 17 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name (8 chars)
6 |  | Rte |  |  | uint32 |  |  | bps | RW | M |  | Rate | Interface baud rate in bits per second
8 |  | Bits |  |  | uint16 |  |  |  | RW | M |  | Bits | Number of data bits per character
9 |  | Pty |  |  | enum16 |  |  |  | RW | M |  | Parity | Bitmask value. Parity setting
|  | NONE | 0
|  | ODD | 1
|  | EVEN | 2
10 |  | Dup |  |  | enum16 |  |  |  | RW |  |  | Duplex | Enumerated value. Duplex mode
|  | FULL | 0
|  | HALF | 1
11 |  | Flw |  |  | enum16 |  |  |  | RW |  |  | Flow Control | Flow Control Method
|  | NONE | 0
|  | HW | 1
|  | XONXOFF | 2
12 |  | Typ |  |  | enum16 | [6 empty] | Interface Type | Enumerated value. Interface type
|  | UNKNOWN | 0
|  | RS232 | 1
|  | RS485 | 2
13 |  | Pcol |  |  | enum16 | [6 empty] | Protocol | Enumerated value. Serial protocol selection
|  | UNKNOWN | 0
|  | MODBUS | 1
|  | VENDOR | 2

## 18
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_18 |  |  | group | [6 empty] | Cellular Link | Include this model to support a cellular interface link
0 |  | ID | 18 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | IMEI |  |  | uint32 |  |  |  | RW |  |  | IMEI | International Mobile Equipment Identifier for the interface
8 |  | APN |  |  | string | 4 |  |  | RW |  |  | APN | Access Point Name for the interface
12 |  | Num |  |  | string | 6 |  |  | RW |  |  | Number | Phone number for the interface
18 |  | Pin |  |  | string | 6 |  |  | RW |  |  | PIN | Personal Identification Number for the interface

## 19
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_19 |  |  | group | [6 empty] | PPP Link | Include this model to configure a Point-to-Point Protocol link
0 |  | ID | 19 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | Rte |  |  | uint32 |  |  | bps | RW | M |  | Rate | Interface baud rate in bits per second
8 |  | Bits |  |  | uint16 |  |  |  | RW | M |  | Bits | Number of data bits per character
9 |  | Pty |  |  | enum16 |  |  |  | RW | M |  | Parity | Bitmask value. Parity setting
|  | NONE | 0
|  | ODD | 1
|  | EVEN | 2
10 |  | Dup |  |  | enum16 |  |  |  | RW |  |  | Duplex | Enumerated value. Duplex mode
|  | FULL | 0
|  | HALF | 1
11 |  | Flw |  |  | enum16 |  |  |  | RW |  |  | Flow Control | Flow Control Method
|  | NONE | 0
|  | HW | 1
|  | XONXOFF | 2
12 |  | Auth |  |  | enum16 | [6 empty] | Authentication | Enumerated value. Authentication method
|  | NONE | 0
|  | PAP | 1
|  | CHAP | 2
13 |  | UsrNam |  |  | string | 12 | [5 empty] | Username | Username for authentication
25 |  | Pw |  |  | string | 6 | [5 empty] | Password | Password for authentication
31 |  | Pad |  |  | pad

## 101
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inverter_single_phase |  |  | group | [6 empty] | Inverter (Single Phase) | Include this model for single phase inverter monitoring
0 |  | ID | 101 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current
3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current | Connected Phase
4 |  | AphB |  |  | uint16 |  | A_SF | A |  |  |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | uint16 |  | A_SF | A |  |  |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M
7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BN | Phase Voltage BN
12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
13 |  | V_SF |  |  | sunssf |  |  |  |  | M
14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power
15 |  | W_SF |  |  | sunssf |  |  |  |  | M
16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency
17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M
18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
19 |  | VA_SF |  |  | sunssf
20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power
21 |  | VAr_SF |  |  | sunssf
22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor
23 |  | PF_SF |  |  | sunssf
24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy
26 |  | WH_SF |  |  | sunssf |  |  |  |  | M
27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current
28 |  | DCA_SF |  |  | sunssf
29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage
30 |  | DCV_SF |  |  | sunssf
31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power
32 |  | DCW_SF |  |  | sunssf
33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature
34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature
37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M
38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 102
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inverter_split_phase |  |  | group | [6 empty] | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
0 |  | ID | 102 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current | Sum of active phases
3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current | Connected Phase
4 |  | AphB |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current | Connected Phase
5 |  | AphC |  |  | uint16 |  | A_SF | A |  |  |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M
7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
13 |  | V_SF |  |  | sunssf |  |  |  |  | M
14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power
15 |  | W_SF |  |  | sunssf |  |  |  |  | M
16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency
17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M
18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
19 |  | VA_SF |  |  | sunssf
20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power
21 |  | VAr_SF |  |  | sunssf
22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor
23 |  | PF_SF |  |  | sunssf
24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy
26 |  | WH_SF |  |  | sunssf |  |  |  |  | M
27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current
28 |  | DCA_SF |  |  | sunssf
29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage
30 |  | DCV_SF |  |  | sunssf
31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power
32 |  | DCW_SF |  |  | sunssf
33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature
34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature
37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M
38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 103
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inverter_three_phase |  |  | group | [6 empty] | Inverter (Three Phase) | Include this model for three phase inverter monitoring
0 |  | ID | 103 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current | Sum of active phases
3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current | Connected Phase
4 |  | AphB |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current | Connected Phase
5 |  | AphC |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current | Connected Phase
6 |  | A_SF |  |  | sunssf |  |  |  |  | M
7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage CN | Phase Voltage CN
13 |  | V_SF |  |  | sunssf |  |  |  |  | M
14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power
15 |  | W_SF |  |  | sunssf |  |  |  |  | M
16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency
17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M
18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
19 |  | VA_SF |  |  | sunssf
20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power
21 |  | VAr_SF |  |  | sunssf
22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor
23 |  | PF_SF |  |  | sunssf
24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy
26 |  | WH_SF |  |  | sunssf |  |  |  |  | M
27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current
28 |  | DCA_SF |  |  | sunssf
29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage
30 |  | DCV_SF |  |  | sunssf
31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power
32 |  | DCW_SF |  |  | sunssf
33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature
34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature
37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M
38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 111
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inverter_single_phase_float |  |  | group | [6 empty] | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
0 |  | ID | 111 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current | Connected Phase
6 |  | AphB |  |  | float32 |  |  | A |  |  |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
12 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
16 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
18 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
20 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
22 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | AC Power
24 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Line Frequency
26 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
28 |  | VAr |  |  | float32 |  |  | var |  |  |  | VAr | AC Reactive Power
30 |  | PF |  |  | float32 |  |  | Pct |  |  |  | PF | AC Power Factor
32 |  | WH |  |  | float32 |  |  | Wh |  | M |  | WattHours | AC Energy
34 |  | DCA |  |  | float32 |  |  | A |  |  |  | DC Amps | DC Current
36 |  | DCV |  |  | float32 |  |  | V |  |  |  | DC Voltage | DC Voltage
38 |  | DCW |  |  | float32 |  |  | W |  |  |  | DC Watts | DC Power
40 |  | TmpCab |  |  | float32 |  |  | C |  | M |  | Cabinet Temperature | Cabinet Temperature
42 |  | TmpSnk |  |  | float32 |  |  | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
44 |  | TmpTrns |  |  | float32 |  |  | C |  |  |  | Transformer Temperature | Transformer Temperature
46 |  | TmpOt |  |  | float32 |  |  | C |  |  |  | Other Temperature | Other Temperature
48 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | ggOFF | 1
|  | ggSLEEPING | 2
|  | ggSTARTING | 3
|  | ggMPPT | 4
|  | ggTHROTTLED | 5
|  | ggSHUTTING_DOWN | 6
|  | ggFAULT | 7
|  | ggSTANDBY | 8
49 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
50 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
52 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
54 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
56 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
58 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
60 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 112
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inverter_split_phase_float |  |  | group | [6 empty] | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
0 |  | ID | 112 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current | Connected Phase
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current | Connected Phase
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
12 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
16 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
18 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
20 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
22 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | AC Power
24 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Line Frequency
26 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
28 |  | VAr |  |  | float32 |  |  | var |  |  |  | VAr | AC Reactive Power
30 |  | PF |  |  | float32 |  |  | Pct |  |  |  | PF | AC Power Factor
32 |  | WH |  |  | float32 |  |  | Wh |  | M |  | WattHours | AC Energy
34 |  | DCA |  |  | float32 |  |  | A |  |  |  | DC Amps | DC Current
36 |  | DCV |  |  | float32 |  |  | V |  |  |  | DC Voltage | DC Voltage
38 |  | DCW |  |  | float32 |  |  | W |  |  |  | DC Watts | DC Power
40 |  | TmpCab |  |  | float32 |  |  | C |  | M |  | Cabinet Temperature | Cabinet Temperature
42 |  | TmpSnk |  |  | float32 |  |  | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
44 |  | TmpTrns |  |  | float32 |  |  | C |  |  |  | Transformer Temperature | Transformer Temperature
46 |  | TmpOt |  |  | float32 |  |  | C |  |  |  | Other Temperature | Other Temperature
48 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
49 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
50 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
52 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
54 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
56 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
58 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
60 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 113
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inverter_three_phase_float |  |  | group | [6 empty] | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
0 |  | ID | 113 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | AC Current | Sum of active phases
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current | Connected Phase
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current | Connected Phase
8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current | Connected Phase
10 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
12 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
16 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
18 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
20 |  | PhVphC |  |  | float32 |  |  | V |  | M |  | Phase Voltage CN | Phase Voltage CN
22 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | AC Power
24 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Line Frequency
26 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
28 |  | VAr |  |  | float32 |  |  | var |  |  |  | VAr | AC Reactive Power
30 |  | PF |  |  | float32 |  |  | Pct |  |  |  | PF | AC Power Factor
32 |  | WH |  |  | float32 |  |  | Wh |  | M |  | WattHours | AC Energy
34 |  | DCA |  |  | float32 |  |  | A |  |  |  | DC Amps | DC Current
36 |  | DCV |  |  | float32 |  |  | V |  |  |  | DC Voltage | DC Voltage
38 |  | DCW |  |  | float32 |  |  | W |  |  |  | DC Watts | DC Power
40 |  | TmpCab |  |  | float32 |  |  | C |  | M |  | Cabinet Temperature | Cabinet Temperature
42 |  | TmpSnk |  |  | float32 |  |  | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
44 |  | TmpTrns |  |  | float32 |  |  | C |  |  |  | Transformer Temperature | Transformer Temperature
46 |  | TmpOt |  |  | float32 |  |  | C |  |  |  | Other Temperature | Other Temperature
48 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
49 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
50 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
52 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
54 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
56 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
58 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
60 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 120
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | nameplate |  |  | group | [6 empty] | Nameplate | Inverter Controls Nameplate Ratings
0 |  | ID | 120 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DERTyp |  |  | enum16 |  |  |  |  | M |  | DERTyp | Type of DER device. Default value is 4 to indicate PV device.
|  | PV | 4
|  | PV_STOR | 82
3 |  | WRtg |  |  | uint16 |  | WRtg_SF | W |  | M |  | WRtg | Continuous power output capability of the inverter.
4 |  | WRtg_SF |  |  | sunssf |  |  |  |  | M |  | WRtg_SF | Scale factor
5 |  | VARtg |  |  | uint16 |  | VARtg_SF | VA |  | M |  | VARtg | Continuous Volt-Ampere capability of the inverter.
6 |  | VARtg_SF |  |  | sunssf |  |  |  |  | M |  | VARtg_SF | Scale factor
7 |  | VArRtgQ1 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1.
8 |  | VArRtgQ2 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2.
9 |  | VArRtgQ3 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3.
10 |  | VArRtgQ4 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4.
11 |  | VArRtg_SF |  |  | sunssf |  |  |  |  | M |  | VArRtg_SF | Scale factor
12 |  | ARtg |  |  | uint16 |  | ARtg_SF | A |  | M |  | ARtg | Maximum RMS AC current level capability of the inverter. | Sum of all connected phases. Current rating under nominal voltage under nominal power factor.
13 |  | ARtg_SF |  |  | sunssf |  |  |  |  | M |  | ARtg_SF | Scale factor
14 |  | PFRtgQ1 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | EEI sign convention.
15 |  | PFRtgQ2 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | EEI sign convention.
16 |  | PFRtgQ3 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | EEI sign convention.
17 |  | PFRtgQ4 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | EEI sign convention.
18 |  | PFRtg_SF |  |  | sunssf |  |  |  |  | M |  | PFRtg_SF | Scale factor
19 |  | WHRtg |  |  | uint16 |  | WHRtg_SF | Wh |  |  |  | WHRtg | Nominal energy rating of storage device.
20 |  | WHRtg_SF |  |  | sunssf | [6 empty] | WHRtg_SF | Scale factor
21 |  | AhrRtg |  |  | uint16 |  | AhrRtg_SF | AH |  |  |  | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
22 |  | AhrRtg_SF |  |  | sunssf | [6 empty] | AhrRtg_SF | Scale factor for amp-hour rating.
23 |  | MaxChaRte |  |  | uint16 |  | MaxChaRte_SF | W |  |  |  | MaxChaRte | Maximum rate of energy transfer into the storage device.
24 |  | MaxChaRte_SF |  |  | sunssf | [6 empty] | MaxChaRte_SF | Scale factor
25 |  | MaxDisChaRte |  |  | uint16 |  | MaxDisChaRte_SF | W |  |  |  | MaxDisChaRte | Maximum rate of energy transfer out of the storage device.
26 |  | MaxDisChaRte_SF |  |  | sunssf | [6 empty] | MaxDisChaRte_SF | Scale factor
27 |  | Pad |  |  | pad | [6 empty] | Pad | Pad register.

## 121
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | settings |  |  | group | [6 empty] | Basic Settings | Inverter Controls Basic Settings
0 |  | ID | 121 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | WMax |  |  | uint16 |  | WMax_SF | W | RW | M |  | WMax | Setting for maximum power output. Default to WRtg.
3 |  | VRef |  |  | uint16 |  | VRef_SF | V | RW | M |  | VRef | Voltage at the PCC.
4 |  | VRefOfs |  |  | int16 |  | VRefOfs_SF | V | RW | M |  | VRefOfs | Offset from PCC to inverter.
5 |  | VMax |  |  | uint16 |  | VMinMax_SF | V | RW |  |  | VMax | Setpoint for maximum voltage.
6 |  | VMin |  |  | uint16 |  | VMinMax_SF | V | RW |  |  | VMin | Setpoint for minimum voltage.
7 |  | VAMax |  |  | uint16 |  | VAMax_SF | VA | RW |  |  | VAMax | Setpoint for maximum apparent power. Default to VARtg.
8 |  | VArMaxQ1 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1.
9 |  | VArMaxQ2 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
10 |  | VArMaxQ3 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
11 |  | VArMaxQ4 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
12 |  | WGra |  |  | uint16 |  | WGra_SF | % WMax/sec | RW |  |  | WGra | Default ramp rate of change of active power due to command or internal action.
13 |  | PFMinQ1 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | EEI sign convention.
14 |  | PFMinQ2 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | EEI sign convention.
15 |  | PFMinQ3 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | EEI sign convention.
16 |  | PFMinQ4 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | EEI sign convention.
17 |  | VArAct |  |  | enum16 |  |  |  | RW |  |  | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
|  | SWITCH | 1
|  | MAINTAIN | 2
18 |  | ClcTotVA |  |  | enum16 |  |  |  | RW |  |  | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic.
|  | VECTOR | 1
|  | ARITHMETIC | 2
19 |  | MaxRmpRte |  |  | uint16 |  | MaxRmpRte_SF | % WGra | RW |  |  | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
20 |  | ECPNomHz |  |  | uint16 |  | ECPNomHz_SF | Hz | RW |  |  | ECPNomHz | Setpoint for nominal frequency at the ECP.
21 |  | ConnPh |  |  | enum16 |  |  |  | RW |  |  | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
|  | A | 1
|  | B | 2
|  | C | 3
22 |  | WMax_SF |  |  | sunssf |  |  |  |  | M |  | WMax_SF | Scale factor for real power.
23 |  | VRef_SF |  |  | sunssf |  |  |  |  | M |  | VRef_SF | Scale factor for voltage at the PCC.
24 |  | VRefOfs_SF |  |  | sunssf |  |  |  |  | M |  | VRefOfs_SF | Scale factor for offset voltage.
25 |  | VMinMax_SF |  |  | sunssf | [6 empty] | VMinMax_SF | Scale factor for min/max voltages.
26 |  | VAMax_SF |  |  | sunssf | [6 empty] | VAMax_SF | Scale factor for apparent power.
27 |  | VArMax_SF |  |  | sunssf | [6 empty] | VArMax_SF | Scale factor for reactive power.
28 |  | WGra_SF |  |  | sunssf | [6 empty] | WGra_SF | Scale factor for default ramp rate.
29 |  | PFMin_SF |  |  | sunssf | [6 empty] | PFMin_SF | Scale factor for minimum power factor.
30 |  | MaxRmpRte_SF |  |  | sunssf | [6 empty] | MaxRmpRte_SF | Scale factor for maximum ramp percentage.
31 |  | ECPNomHz_SF |  |  | sunssf | [6 empty] | ECPNomHz_SF | Scale factor for nominal frequency.

## 122
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | status |  |  | group | [6 empty] | Measurements_Status | Inverter Controls Extended Measurements and Status
0 |  | ID | 122 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | PVConn |  |  | bitfield16 |  |  |  |  | M |  | PVConn | PV inverter present/available status. Enumerated value.
|  | CONNECTED | 0
|  | AVAILABLE | 1
|  | OPERATING | 2
|  | TEST | 3
3 |  | StorConn |  |  | bitfield16 |  |  |  |  | M |  | StorConn | Storage inverter present/available status. Enumerated value.
|  | CONNECTED | 0
|  | AVAILABLE | 1
|  | OPERATING | 2
|  | TEST | 3
4 |  | ECPConn |  |  | bitfield16 |  |  |  |  | M |  | ECPConn | ECP connection status: disconnected=0 connected=1.
|  | DISCONNECTED | 0
|  | CONNECTED | 1
5 |  | ActWh |  |  | acc64 |  |  | Wh |  |  |  | ActWh | AC lifetime active (real) energy output.
9 |  | ActVAh |  |  | acc64 |  |  | VAh |  |  |  | ActVAh | AC lifetime apparent energy output.
13 |  | ActVArhQ1 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1.
17 |  | ActVArhQ2 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2.
21 |  | ActVArhQ3 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ3 | AC lifetime negative energy output in quadrant 3.
25 |  | ActVArhQ4 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4.
29 |  | VArAval |  |  | int16 |  | VArAval_SF | var |  |  |  | VArAval | Amount of VARs available without impacting watts output.
30 |  | VArAval_SF |  |  | sunssf | [6 empty] | VArAval_SF | Scale factor for available VARs.
31 |  | WAval |  |  | uint16 |  | WAval_SF | var |  |  |  | WAval | Amount of Watts available.
32 |  | WAval_SF |  |  | sunssf | [6 empty] | WAval_SF | Scale factor for available Watts.
33 |  | StSetLimMsk |  |  | bitfield32 | [6 empty] | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | Bits shall be automatically cleared on read.
|  | WMax | 0
|  | VAMax | 1
|  | VArAval | 2
|  | VArMaxQ1 | 3
|  | VArMaxQ2 | 4
|  | VArMaxQ3 | 5
|  | VArMaxQ4 | 6
|  | PFMinQ1 | 7
|  | PFMinQ2 | 8
|  | PFMinQ3 | 9
|  | PFMinQ4 | 10
35 |  | StActCtl |  |  | bitfield32 | [6 empty] | StActCtl | Bit Mask indicating which inverter controls are currently active.
|  | FixedW | 0
|  | FixedVAR | 1
|  | FixedPF | 2
|  | Volt-VAr | 3
|  | Freq-Watt-Param | 4
|  | Freq-Watt-Curve | 5
|  | Dyn-Reactive-Current | 6
|  | LVRT | 7
|  | HVRT | 8
|  | Watt-PF | 9
|  | Volt-Watt | 10
|  | Scheduled | 12
|  | LFRT | 13
|  | HFRT | 14
37 |  | TmSrc |  |  | string | 4 | [5 empty] | TmSrc | Source of time synchronization.
41 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Tms | Seconds since 01-01-2000 00:00 UTC
43 |  | RtSt |  |  | bitfield16 | [6 empty] | RtSt | Bit Mask indicating active ride-through status.
|  | LVRT_ACTIVE | 0
|  | HVRT_ACTIVE | 1
|  | LFRT_ACTIVE | 2
|  | HFRT_ACTIVE | 3
44 |  | Ris |  |  | uint16 |  | Ris_SF | ohms |  |  |  | Ris | Isolation resistance.
45 |  | Ris_SF |  |  | sunssf | [6 empty] | Ris_SF | Scale factor for isolation resistance.

## 123
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | controls |  |  | group | [6 empty] | Immediate Controls | Immediate Inverter Controls
0 |  | ID | 123 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Conn_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | Conn_WinTms | Time window for connect/disconnect.
3 |  | Conn_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | Conn_RvrtTms | Timeout period for connect/disconnect.
4 |  | Conn |  |  | enum16 |  |  |  | RW | M |  | Conn | Enumerated valued. Connection control.
|  | DISCONNECT | 0
|  | CONNECT | 1
5 |  | WMaxLimPct |  |  | uint16 |  | WMaxLimPct_SF | % WMax | RW | M |  | WMaxLimPct | Set power output to specified level.
6 |  | WMaxLimPct_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_WinTms | Time window for power limit change.
7 |  | WMaxLimPct_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_RvrtTms | Timeout period for power limit.
8 |  | WMaxLimPct_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint.
9 |  | WMaxLim_Ena |  |  | enum16 |  |  |  | RW | M |  | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
10 |  | OutPFSet |  |  | int16 |  | OutPFSet_SF | cos() | RW | M |  | OutPFSet | Set power factor to specific value - cosine of angle.
11 |  | OutPFSet_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_WinTms | Time window for power factor change.
12 |  | OutPFSet_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_RvrtTms | Timeout period for power factor.
13 |  | OutPFSet_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint.
14 |  | OutPFSet_Ena |  |  | enum16 |  |  |  | RW | M |  | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
15 |  | VArWMaxPct |  |  | int16 |  | VArPct_SF | % WMax | RW |  |  | VArWMaxPct | Reactive power in percent of WMax.
16 |  | VArMaxPct |  |  | int16 |  | VArPct_SF | % VArMax | RW |  |  | VArMaxPct | Reactive power in percent of VArMax.
17 |  | VArAvalPct |  |  | int16 |  | VArPct_SF | % VArAval | RW |  |  | VArAvalPct | Reactive power in percent of VArAval.
18 |  | VArPct_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_WinTms | Time window for VAR limit change.
19 |  | VArPct_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_RvrtTms | Timeout period for VAR limit.
20 |  | VArPct_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint.
21 |  | VArPct_Mod |  |  | enum16 |  |  |  | RW |  |  | VArPct_Mod | Enumerated value. VAR percent limit mode.
|  | NONE | 0
|  | WMax | 1
|  | VArMax | 2
|  | VArAval | 3
22 |  | VArPct_Ena |  |  | enum16 |  |  |  | RW | M |  | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
23 |  | WMaxLimPct_SF |  |  | sunssf |  |  |  |  | M |  | WMaxLimPct_SF | Scale factor for power output percent.
24 |  | OutPFSet_SF |  |  | sunssf |  |  |  |  | M |  | OutPFSet_SF | Scale factor for power factor.
25 |  | VArPct_SF |  |  | sunssf | [6 empty] | VArPct_SF | Scale factor for reactive power percent.

## 124
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | storage_basic |  |  | group | [6 empty] | Storage | Basic Storage Controls
0 |  | ID | 124 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | WChaMax |  |  | uint16 |  | WChaMax_SF | W | RW | M |  | WChaMax | Setpoint for maximum charge.
3 |  | WChaGra |  |  | uint16 |  | WChaDisChaGra_SF | % WChaMax/sec | RW | M |  | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte.
4 |  | WDisChaGra |  |  | uint16 |  | WChaDisChaGra_SF | % WChaMax/sec | RW | M |  | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte.
5 |  | StorCtl_Mod |  |  | bitfield16 |  |  |  | RW | M |  | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value.
|  | CHARGE | 0
|  | DiSCHARGE | 1
6 |  | VAChaMax |  |  | uint16 |  | VAChaMax_SF | VA | RW |  |  | VAChaMax | Setpoint for maximum charging VA.
7 |  | MinRsvPct |  |  | uint16 |  | MinRsvPct_SF | % WChaMax | RW |  |  | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
8 |  | ChaState |  |  | uint16 |  | ChaState_SF | % AhrRtg |  |  |  | ChaState | Currently available energy as a percent of the capacity rating.
9 |  | StorAval |  |  | uint16 |  | StorAval_SF | AH |  |  |  | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg).
10 |  | InBatV |  |  | uint16 |  | InBatV_SF | V |  |  |  | InBatV | Internal battery voltage.
11 |  | ChaSt |  |  | enum16 | [6 empty] | ChaSt | Charge status of storage device. Enumerated value.
|  | OFF | 1
|  | EMPTY | 2
|  | DISCHARGING | 3
|  | CHARGING | 4
|  | FULL | 5
|  | HOLDING | 6
|  | TESTING | 7
12 |  | OutWRte |  |  | int16 |  | InOutWRte_SF | % WDisChaMax | RW |  |  | OutWRte | Percent of max discharge rate.
13 |  | InWRte |  |  | int16 |  | InOutWRte_SF | % WChaMax | RW |  |  | InWRte | Percent of max charging rate.
14 |  | InOutWRte_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_WinTms | Time window for charge/discharge rate change.
15 |  | InOutWRte_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_RvrtTms | Timeout period for charge/discharge rate.
16 |  | InOutWRte_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint.
17 |  | ChaGriSet |  |  | enum16 |  |  |  | RW
|  | PV | 0
|  | GRID | 1
18 |  | WChaMax_SF |  |  | sunssf |  |  |  |  | M |  | WChaMax_SF | Scale factor for maximum charge.
19 |  | WChaDisChaGra_SF |  |  | sunssf |  |  |  |  | M |  | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate.
20 |  | VAChaMax_SF |  |  | sunssf | [6 empty] | VAChaMax_SF | Scale factor for maximum charging VA.
21 |  | MinRsvPct_SF |  |  | sunssf | [6 empty] | MinRsvPct_SF | Scale factor for minimum reserve percentage.
22 |  | ChaState_SF |  |  | sunssf | [6 empty] | ChaState_SF | Scale factor for available energy percent.
23 |  | StorAval_SF |  |  | sunssf | [6 empty] | StorAval_SF | Scale factor for state of charge.
24 |  | InBatV_SF |  |  | sunssf | [6 empty] | InBatV_SF | Scale factor for battery voltage.
25 |  | InOutWRte_SF |  |  | sunssf | [6 empty] | InOutWRte_SF | Scale factor for percent charge/discharge rate.

## 125
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | pricing |  |  | group | [6 empty] | Pricing | Pricing Signal
0 |  | ID | 125 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is price-based charge/discharge mode active?
|  | ENABLE | 0
3 |  | SigType |  |  | enum16 |  |  |  | RW |  |  | SigType | Meaning of the pricing signal. When a Price schedule is used, type must match the schedule range variable description.
|  | UNKNOWN | 0
|  | ABSOLUTE | 1
|  | RELATIVE | 2
|  | MULTIPLIER | 3
|  | LEVEL | 4
4 |  | Sig |  |  | int16 |  | Sig_SF |  | RW | M |  | Sig | Utility/ESP specific pricing signal. Content depends on pricing signal type. When H/M/L type is specified. Low=0; Med=1; High=2.
5 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for charge/discharge pricing change.
6 |  | RvtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvtTms | Timeout period for charge/discharge pricing change.
7 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current charge or discharge level to new level.
8 |  | Sig_SF |  |  | sunssf |  |  |  |  | M |  | Sig_SF | Pricing signal scale factor.
9 |  | Pad |  |  | pad

## 126
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | volt_var |  |  | group | [6 empty] | Static Volt-VAR | Static Volt-VAR Arrays
0 |  | ID | 126 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is Volt-VAR control active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for volt-VAR change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for volt-VAR curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | The time of the PT1 in seconds (time to accomplish a change of 95%).
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
10 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M |  | DeptRef_SF | scale factor for dependent variable.
11 |  | RmpIncDec_SF |  |  | sunssf
|  | volt_var.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval.
|  | WMax | 1
|  | VArMax | 2
|  | VArAval | 3
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 Volts.
| 3 | VAr1 |  |  | int16 |  | DeptRef_SF |  | RW | M |  | VAr1 | Point 1 VARs.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 Volts.
| 5 | VAr2 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr2 | Point 2 VARs.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 Volts.
| 7 | VAr3 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr3 | Point 3 VARs.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 Volts.
| 9 | VAr4 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr4 | Point 4 VARs.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 Volts.
| 11 | VAr5 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr5 | Point 5 VARs.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 Volts.
| 13 | VAr6 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr6 | Point 6 VARs.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 Volts.
| 15 | VAr7 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr7 | Point 7 VARs.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 Volts.
| 17 | VAr8 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr8 | Point 8 VARs.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 Volts.
| 19 | VAr9 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr9 | Point 9 VARs.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 Volts.
| 21 | VAr10 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr10 | Point 10 VARs.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 Volts.
| 23 | VAr11 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr11 | Point 11 VARs.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 Volts.
| 25 | VAr12 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr12 | Point 12 VARs.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 Volts.
| 27 | VAr13 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr13 | Point 13 VARs.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 Volts.
| 29 | VAr14 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr14 | Point 14 VARs.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 Volts.
| 31 | VAr15 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr15 | Point 15 VARs.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 Volts.
| 33 | VAr16 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr16 | Point 16 VARs.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 Volts.
| 35 | VAr17 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr17 | Point 17 VARs.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 Volts.
| 37 | VAr18 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr18 | Point 18 VARs.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 Volts.
| 39 | VAr19 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr19 | Point 19 VARs.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 Volts.
| 41 | VAr20 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr20 | Point 20 VARs.
| 42 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve. (Max 16 chars)
| 50 | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 51 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % ref_value/min | RW |  |  | RmpDecTmm | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
| 52 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % ref_value/min | RW |  |  | RmpIncTmm | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
| 53 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Boolean flag indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 127
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | freq_watt_param |  |  | group | [6 empty] | Freq-Watt Param | Parameterized Frequency-Watt
0 |  | ID | 127 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | WGra |  |  | uint16 |  | WGra_SF | % PM/Hz | RW | M |  | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency.
3 |  | HzStr |  |  | int16 |  | HzStrStop_SF | Hz | RW | M |  | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
4 |  | HzStop |  |  | int16 |  | HzStrStop_SF | Hz | RW | M |  | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
5 |  | HysEna |  |  | bitfield16 |  |  |  | RW | M |  | HysEna | Enable hysteresis
|  | ENABLED | 0
6 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is Parameterized Frequency-Watt control active.
|  | ENABLED | 0
7 |  | HzStopWGra |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
8 |  | WGra_SF |  |  | sunssf | [6 empty] | WGra_SF | Scale factor for output gradient.
9 |  | HzStrStop_SF |  |  | sunssf | [6 empty] | HzStrStop_SF | Scale factor for frequency deviations.
10 |  | RmpIncDec_SF |  |  | sunssf | [6 empty] | RmpIncDec_SF | Scale factor for increment and decrement ramps.
11 |  | Pad |  |  | pad

## 128
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | reactive_current |  |  | group | [6 empty] | Dynamic Reactive Current | Dynamic Reactive Current
0 |  | ID | 128 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ArGraMod |  |  | enum16 |  |  |  | RW | M |  | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband.
|  | EDGE | 0
|  | CENTER | 1
3 |  | ArGraSag |  |  | uint16 |  | ArGra_SF | %ARtg/%dV | RW | M |  | ArGraSag | The gradient used to increase capacitive dynamic current. A value of 0 indicates no additional reactive current support.
4 |  | ArGraSwell |  |  | uint16 |  | ArGra_SF | %ARtg/%dV | RW | M |  | ArGraSwell | The gradient used to increase inductive dynamic current. A value of 0 indicates no additional reactive current support.
5 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Activate dynamic reactive current model
|  | ENABLED | 0
6 |  | FilTms |  |  | uint16 |  |  | Secs | RW |  |  | FilTms | The time window used to calculate the moving average voltage.
7 |  | DbVMin |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced.
8 |  | DbVMax |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced.
9 |  | BlkZnV |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced.
10 |  | HysBlkZnV |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | HysBlkZnV | Hysteresis voltage used with BlkZnV.
11 |  | BlkZnTmms |  |  | uint16 |  |  | mSecs | RW |  |  | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops.
12 |  | HoldTmms |  |  | uint16 |  |  | mSecs | RW |  |  | HoldTmms | Hold time during which reactive current support continues after the average voltage has entered the dead zone.
13 |  | ArGra_SF |  |  | sunssf |  |  |  |  | M |  | ArGra_SF | Scale factor for the gradients.
14 |  | VRefPct_SF |  |  | sunssf | [6 empty] | VRefPct_SF | Scale factor for the voltage zone and limit settings.
15 |  | Pad |  |  | pad

## 129
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lvrt |  |  | group | [6 empty] | LVRTD | LVRT Must Disconnect
0 |  | ID | 129 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change. | Setting is ignored for LVRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | lvrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must disconnect voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must disconnect voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must disconnect voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must disconnect voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must disconnect voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must disconnect voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must disconnect voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must disconnect voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must disconnect voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must disconnect voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must disconnect voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must disconnect voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must disconnect voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must disconnect voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must disconnect voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must disconnect voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must disconnect voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must disconnect voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must disconnect voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must disconnect voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 130
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | hvrt |  |  | group | [6 empty] | HVRTD | HVRT Must Disconnect
0 |  | ID | 130 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | HVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for HVRT change. | Setting is ignored for HVRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | hvrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must disconnect voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must disconnect voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must disconnect voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must disconnect voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must disconnect voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must disconnect voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must disconnect voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must disconnect voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must disconnect voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must disconnect voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must disconnect voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must disconnect voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must disconnect voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must disconnect voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must disconnect voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must disconnect voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must disconnect voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must disconnect voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must disconnect voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must disconnect voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 131
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | watt_pf |  |  | group | [6 empty] | Watt-PF | Watt-Power Factor
0 |  | ID | 131 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is watt-PF mode active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for watt-PF change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for watt-PF curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Max number of points in array.
9 |  | W_SF |  |  | sunssf |  |  |  |  | M |  | W_SF | Scale factor for percent WMax.
10 |  | PF_SF |  |  | sunssf |  |  |  |  | M |  | PF_SF | Scale factor for PF.
11 |  | RmpIncDec_SF |  |  | sunssf | [6 empty] | RmpIncDec_SF | Scale factor for increment and decrement ramps.
|  | watt_pf.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | W1 |  |  | int16 |  | W_SF | % WMax | RW | M |  | W1 | Point 1 Watts.
| 2 | PF1 |  |  | int16 |  | PF_SF | cos() | RW | M |  | PF1 | Point 1 PF in EEI notation.
| 3 | W2 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W2 | Point 2 Watts.
| 4 | PF2 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF2 | Point 2 PF in EEI notation.
| 5 | W3 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W3 | Point 3 Watts.
| 6 | PF3 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF3 | Point 3 PF in EEI notation.
| 7 | W4 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W4 | Point 4 Watts.
| 8 | PF4 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF4 | Point 4 PF in EEI notation.
| 9 | W5 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W5 | Point 5 Watts.
| 10 | PF5 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF5 | Point 5 PF in EEI notation.
| 11 | W6 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W6 | Point 6 Watts.
| 12 | PF6 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF6 | Point 6 PF in EEI notation.
| 13 | W7 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W7 | Point 7 Watts.
| 14 | PF7 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF7 | Point 7 PF in EEI notation.
| 15 | W8 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W8 | Point 8 Watts.
| 16 | PF8 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF8 | Point 8 PF in EEI notation.
| 17 | W9 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W9 | Point 9 Watts.
| 18 | PF9 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF9 | Point 9 PF in EEI notation.
| 19 | W10 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W10 | Point 10 Watts.
| 20 | PF10 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF10 | Point 10 PF in EEI notation.
| 21 | W11 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W11 | Point 11 Watts.
| 22 | PF11 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF11 | Point 11 PF in EEI notation.
| 23 | W12 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W12 | Point 12 Watts.
| 24 | PF12 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF12 | Point 12 PF in EEI notation.
| 25 | W13 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W13 | Point 13 Watts.
| 26 | PF13 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF13 | Point 13 PF in EEI notation.
| 27 | W14 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W14 | Point 14 Watts.
| 28 | PF14 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF14 | Point 14 PF in EEI notation.
| 29 | W15 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W15 | Point 15 Watts.
| 30 | PF15 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF15 | Point 15 PF in EEI notation.
| 31 | W16 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W16 | Point 16 Watts.
| 32 | PF16 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF16 | Point 16 PF in EEI notation.
| 33 | W17 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W17 | Point 17 Watts.
| 34 | PF17 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF17 | Point 17 PF in EEI notation.
| 35 | W18 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W18 | Point 18 Watts.
| 36 | PF18 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF18 | Point 18 PF in EEI notation.
| 37 | W19 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W19 | Point 19 Watts.
| 38 | PF19 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF19 | Point 19 PF in EEI notation.
| 39 | W20 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W20 | Point 20 Watts.
| 40 | PF20 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF20 | Point 20 PF in EEI notation.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | RmpPT1Tms |  |  | uint16 |  |  | Secs | RW |  |  | RmpPT1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 50 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % PF/min | RW |  |  | RmpDecTmm | The maximum rate at which the power factor may be reduced in response to changes in the power value.
| 51 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % PF/min | RW |  |  | RmpIncTmm | The maximum rate at which the power factor may be increased in response to changes in the power value.
| 52 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1
| 53 | Pad |  |  | pad

## 132
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | volt_watt |  |  | group | [6 empty] | Volt-Watt | Volt-Watt
0 |  | ID | 132 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is Volt-Watt control active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for volt-watt change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for volt-watt curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend min. 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of points in array (maximum 20).
9 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
10 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M |  | DeptRef_SF | Scale Factor for % DeptRef
11 |  | RmpIncDec_SF |  |  | sunssf | [6 empty] | RmpIncDec_SF | Scale factor for increment and decrement ramps.
|  | volt_watt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail
|  | %WMax | 1
|  | %WAval | 2
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 Volts.
| 3 | W1 |  |  | int16 |  | DeptRef_SF | % VRef | RW | M |  | W1 | Point 1 Watts.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 Volts.
| 5 | W2 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W2 | Point 2 Watts.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 Volts.
| 7 | W3 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W3 | Point 3 Watts.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 Volts.
| 9 | W4 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W4 | Point 4 Watts.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 Volts.
| 11 | W5 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W5 | Point 5 Watts.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 Volts.
| 13 | W6 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W6 | Point 6 Watts.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 Volts.
| 15 | W7 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W7 | Point 7 Watts.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 Volts.
| 17 | W8 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W8 | Point 8 Watts.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 Volts.
| 19 | W9 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W9 | Point 9 Watts.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 Volts.
| 21 | W10 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W10 | Point 10 Watts.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 Volts.
| 23 | W11 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W11 | Point 11 Watts.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 Volts.
| 25 | W12 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W12 | Point 12 Watts.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 Volts.
| 27 | W13 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W13 | Point 13 Watts.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 Volts.
| 29 | W14 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W14 | Point 14 Watts.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 Volts.
| 31 | W15 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W15 | Point 15 Watts.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 Volts.
| 33 | W16 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W16 | Point 16 Watts.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 Volts.
| 35 | W17 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W17 | Point 17 Watts.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 Volts.
| 37 | W18 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W18 | Point 18 Watts.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 Volts.
| 39 | W19 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W19 | Point 19 Watts.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 Volts.
| 41 | W20 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W20 | Point 20 Watts.
| 42 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 50 | RmpPt1Tms |  |  | uint16 |  |  | Secs | RW |  |  | RmpPt1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 51 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpDecTmm | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
| 52 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpIncTmm | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
| 53 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 133
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | schedule |  |  | group | [6 empty] | Basic Scheduling | Basic Scheduling
0 |  | ID | 133 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActSchd |  |  | bitfield32 |  |  |  | RW | M |  | ActSchd | Bitfield of active schedules
|  | SCHED1 | 0
|  | SCHED2 | 1
|  | SCHED3 | 2
|  | SCHED4 | 3
|  | SCHED5 | 4
|  | SCHED6 | 5
|  | SCHED7 | 6
|  | SCHED8 | 7
|  | SCHED9 | 8
|  | SCHED10 | 9
|  | SCHED12 | 10
|  | SCHED13 | 11
|  | SCHED14 | 12
|  | SCHED15 | 13
|  | SCHED16 | 14
|  | SCHED17 | 15
|  | SCHED18 | 16
|  | SCHED19 | 17
|  | SCHED20 | 18
|  | SCHED21 | 19
|  | SCHED22 | 21
|  | SCHED23 | 22
|  | SCHED24 | 23
|  | SCHED25 | 24
|  | SCHED26 | 25
|  | SCHED27 | 26
|  | SCHED28 | 27
|  | SCHED29 | 28
|  | SCHED30 | 29
|  | SCHED31 | 30
|  | SCHED32 | 31
4 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is basic scheduling active.
|  | ENABLED | 0
5 |  | NSchd |  |  | uint16 |  |  |  |  | M |  | NSchd | Number of schedules supported (recommend min. 4, max 32)
6 |  | NPts |  |  | uint16 |  |  |  |  | M |  | NPts | Number of schedule entries supported (maximum of 10).
7 |  | Pad |  |  | pad | [6 empty] | Pad | Pad register.
|  | schedule.repeating |  | 0 | group
| 0 | ActPts |  |  | uint16 |  |  |  | RW | M |  | ActPts | Number of active entries in schedule.
| 1 | StrTms |  |  | uint32 |  |  | Secs | RW | M |  | StrTms | Schedule start in seconds since 2000 JAN 01 00:00:00 UTC.
| 3 | RepPer |  |  | uint16 |  |  |  | RW | M |  | RepPer | The repetition count for time-based schedules (0=repeat forever)
| 4 | IntvTyp |  |  | enum16 |  |  |  | RW | M |  | SchdTyp | The repetition frequency for time-based schedules: no repeat=0
|  | ONETIME | 0
|  | DAILY | 1
|  | WEEKLY | 2
|  | MONTHLY | 3
|  | WEEKDAY | 4
|  | HOLIDAY | 5
|  | WEEKEND | 6
|  | YEARLY | 7
| 5 | XTyp |  |  | enum16 |  |  |  | RW | M |  | XTyp | The meaning of the X-values in the array.
|  | UNSET | 0
|  | TIME | 1
|  | TEMP | 2
|  | PRICE | 3
|  | OTHER | 99
| 6 | X_SF |  |  | sunssf |  |  |  | RW | M |  | X_SF | Scale factor for schedule range values.
| 7 | YTyp |  |  | enum16 |  |  |  | RW | M |  | YTyp | The meaning of the Y-values in the array.
|  | UNSET | 0
|  | WMax | 1
|  | RSRVD2 | 2
|  | PF | 3
|  | RSRVD4 | 4
|  | WATT_PRICE | 5
|  | VAR_PRICE | 6
|  | RSRVD7 | 7
|  | VOLT_VAR_ARRAY | 8
|  | WChaGra | 9
|  | WDisChaGra | 10
|  | VArAval | 11
|  | Schedule | 12
|  | OTHER | 99
| 8 | Y_SF |  |  | sunssf |  |  |  | RW | M |  | Y_SF | Scale factor for schedule target values.
| 9 | X1 |  |  | int32 |  | X_SF |  | RW | M |  | X1 | Entry 1 range.
| 11 | Y1 |  |  | int32 |  | Y_SF |  | RW | M |  | Y1 | Entry 1 target.
| 13 | X2 |  |  | int32 |  | X_SF |  | RW |  |  | X2 | Entry 2 range.
| 15 | Y2 |  |  | int32 |  | Y_SF |  | RW |  |  | Y2 | Entry 2 target.
| 17 | X3 |  |  | int32 |  | X_SF |  | RW |  |  | X3 | Entry 3 range.
| 19 | Y3 |  |  | int32 |  | Y_SF |  | RW |  |  | Y3 | Entry 3 target.
| 21 | X4 |  |  | int32 |  | X_SF |  | RW |  |  | X4 | Entry 4 range.
| 23 | Y4 |  |  | int32 |  | Y_SF |  | RW |  |  | Y4 | Entry 4 target.
| 25 | X5 |  |  | int32 |  | X_SF |  | RW |  |  | X5 | Entry 15range.
| 27 | Y5 |  |  | int32 |  | Y_SF |  | RW |  |  | Y5 | Entry 5 target.
| 29 | X6 |  |  | int32 |  | X_SF |  | RW |  |  | X6 | Entry 6 range.
| 31 | Y6 |  |  | int32 |  | Y_SF |  | RW |  |  | Y6 | Entry 6 target.
| 33 | X7 |  |  | int32 |  | X_SF |  | RW |  |  | X7 | Entry 7 range.
| 35 | Y7 |  |  | int32 |  | Y_SF |  | RW |  |  | Y7 | Entry 7 target.
| 37 | X8 |  |  | int32 |  | X_SF |  | RW |  |  | X8 | Entry 8 range.
| 39 | Y8 |  |  | int32 |  | Y_SF |  | RW |  |  | Y8 | Entry 8 target.
| 41 | X9 |  |  | int32 |  | X_SF |  | RW |  |  | X9 | Entry 9 range.
| 43 | Y9 |  |  | int32 |  | Y_SF |  | RW |  |  | Y9 | Entry 9 target.
| 45 | X10 |  |  | int32 |  | X_SF |  | RW |  |  | X10 | Entry 10 range.
| 47 | Y10 |  |  | int32 |  | Y_SF |  | RW |  |  | Y10 | Entry 10 target.
| 49 | Nam |  |  | string | 8 |  |  | RW |  |  | Nam | Optional description for schedule.
| 57 | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for schedule entry change.
| 58 | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current target to new target.
| 59 | ActIndx |  |  | uint16 |  |  |  |  | M |  | ActIndx | Index of active entry in the active schedule.

## 134
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | freq_watt |  |  | group | [6 empty] | Freq-Watt Crv | Curve-Based Frequency-Watt
0 |  | ID | 134 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is curve-based Frequency-Watt control active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for freq-watt change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for freq-watt curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend min. 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Hz_SF |  |  | sunssf |  |  | SF |  | M |  | Hz_SF | Scale factor for frequency.
10 |  | W_SF |  |  | sunssf |  |  | SF |  | M |  | W_SF | Scale factor for percent WRef.
11 |  | RmpIncDec_SF |  |  | sunssf |  |  | SF |  |  |  | RmpIncDec_SF | Scale factor for increment and decrement ramps.
|  | freq_watt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 Hertz.
| 2 | W1 |  |  | int16 |  | W_SF | % WRef | RW | M |  | W1 | Point 1 Watts.
| 3 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 Hertz.
| 4 | W2 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W2 | Point 2 Watts.
| 5 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 Hertz.
| 6 | W3 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W3 | Point 3 Watts.
| 7 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 Hertz.
| 8 | W4 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W4 | Point 4 Watts.
| 9 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 Hertz.
| 10 | W5 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W5 | Point 5 Watts.
| 11 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 Hertz.
| 12 | W6 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W6 | Point 6 Watts.
| 13 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 Hertz.
| 14 | W7 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W7 | Point 7 Watts.
| 15 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 Hertz.
| 16 | W8 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W8 | Point 8 Watts.
| 17 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 Hertz.
| 18 | W9 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W9 | Point 9 Watts.
| 19 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 Hertz.
| 20 | W10 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W10 | Point 10 Watts.
| 21 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 Hertz.
| 22 | W11 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W11 | Point 11 Watts.
| 23 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 Hertz.
| 24 | W12 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W12 | Point 12 Watts.
| 25 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 Hertz.
| 26 | W13 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W13 | Point 13 Watts.
| 27 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 Hertz.
| 28 | W14 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W14 | Point 14 Watts.
| 29 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 Hertz.
| 30 | W15 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W15 | Point 15 Watts.
| 31 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 Hertz.
| 32 | W16 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W16 | Point 16 Watts.
| 33 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 Hertz.
| 34 | W17 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W17 | Point 17 Watts.
| 35 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 Hertz.
| 36 | W18 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W18 | Point 18 Watts.
| 37 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 Hertz.
| 38 | W19 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W19 | Point 19 Watts.
| 39 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 Hertz.
| 40 | W20 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W20 | Point 20 Watts.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve. (Max 16 chars)
| 49 | RmpPT1Tms |  |  | uint16 |  |  | Secs | RW |  |  | RmpPT1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 50 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpDecTmm | The maximum rate at which the power value may be reduced in response to changes in the frequency value.
| 51 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpIncTmm | The maximum rate at which the power value may be increased in response to changes in the frequency value.
| 52 | RmpRsUp |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpRsUp | The maximum rate at which the power may be increased after releasing the frozen value of snap shot function.
| 53 | SnptW |  |  | bitfield16 |  |  |  | RW | M |  | SnptW | 1=enable snapshot/capture mode
| 54 | WRef |  |  | uint16 |  | W_SF | W | RW |  |  | WRef | Reference active power (default = WMax).
| 55 | WRefStrHz |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | WRefStrHz | Frequency deviation from nominal frequency at the time of the snapshot to start constraining power output.
| 56 | WRefStopHz |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | WRefStopHz | Frequency deviation from nominal frequency at which to release the power output.
| 57 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 135
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lfrt |  |  | group | [6 empty] | LFRT | Low Frequency Ride-through
0 |  | ID | 135 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change. | Setting is ignored for LFRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | lfrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must disconnect frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must disconnect frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must disconnect frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must disconnect frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must disconnect frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must disconnect frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must disconnect frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must disconnect frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must disconnect frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must disconnect frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must disconnect frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must disconnect frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must disconnect frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must disconnect frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must disconnect frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must disconnect frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must disconnect frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must disconnect frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must disconnect frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must disconnect frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 136
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | hfrt |  |  | group | [6 empty] | HFRT | High Frequency Ride-through
0 |  | ID | 136 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | HFRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for HFRT change. | Setting is ignored for HFRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for HFRT curve selection. | Setting is ignored for HFRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for HFRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | hfrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must disconnect frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must disconnect frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must disconnect frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must disconnect frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must disconnect frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must disconnect frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must disconnect frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must disconnect frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must disconnect frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must disconnect frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must disconnect frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must disconnect frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must disconnect frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must disconnect frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must disconnect frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must disconnect frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must disconnect frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must disconnect frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must disconnect frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must disconnect frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 137
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lvrtc |  |  | group | [6 empty] | LVRTC | LVRT must remain connected
0 |  | ID | 137 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change. | Setting is ignored for LVRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | lvrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must remain connected voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must remain connected voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must remain connected voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must remain connected voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must remain connected voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must remain connected voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must remain connected voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must remain connected voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must remain connected voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must remain connected voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must remain connected voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must remain connected voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must remain connected voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must remain connected voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must remain connected voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must remain connected voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must remain connected voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must remain connected voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must remain connected voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must remain connected voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 138
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | hvrtc |  |  | group | [6 empty] | HVRTC | HVRT must remain connected
0 |  | ID | 138 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | HVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for HVRT change. | Setting is ignored for HVRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | hvrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must remain connected voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must remain connected voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must remain connected voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must remain connected voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must remain connected voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must remain connected voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must remain connected voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must remain connected voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must remain connected voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must remain connected voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must remain connected voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must remain connected voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must remain connected voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must remain connected voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must remain connected voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must remain connected voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must remain connected voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must remain connected voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must remain connected voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must remain connected voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 139
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lvrtx |  |  | group | [6 empty] | LVRTX | LVRT extended curve
0 |  | ID | 139 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change. | Setting is ignored for LVRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | lvrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 140
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | hvrtx |  |  | group | [6 empty] | HVRTX | HVRT extended curve
0 |  | ID | 140 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change. | Setting is ignored for LVRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | hvrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 141
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lfrtc |  |  | group | [6 empty] | LFRTC | LFRT must remain connected
0 |  | ID | 141 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change. | Setting is ignored for LFRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | lfrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must remain connected frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must remain connected frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must remain connected frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must remain connected frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must remain connected frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must remain connected frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must remain connected frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must remain connected frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must remain connected frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must remain connected frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must remain connected frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must remain connected frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must remain connected frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must remain connected frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must remain connected frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must remain connected frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must remain connected frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must remain connected frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must remain connected frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must remain connected frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 142
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | hfrtc |  |  | group | [6 empty] | HFRTC | HFRT must remain connected
0 |  | ID | 142 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change. | Setting is ignored for LFRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | hfrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must remain connected frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must remain connected frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must remain connected frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must remain connected frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must remain connected frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must remain connected frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must remain connected frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must remain connected frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must remain connected frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must remain connected frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must remain connected frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must remain connected frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must remain connected frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must remain connected frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must remain connected frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must remain connected frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must remain connected frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must remain connected frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must remain connected frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must remain connected frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 143
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lfrtx |  |  | group | [6 empty] | LFRTX | LFRT extended curve
0 |  | ID | 143 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change. | Setting is ignored for LFRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | lfrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 144
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | hfrtx |  |  | group | [6 empty] | HFRTX | HFRT extended curve
0 |  | ID | 144 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change. | Setting is ignored for LFRT controls.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | hfrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 145
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ext_settings |  |  | group | [6 empty] | Extended Settings | Inverter controls extended settings
0 |  | ID | 145 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | NomRmpUpRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Ramp Up Rate | Ramp up rate as a percentage of max current.
3 |  | NomRmpDnRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | NomRmpDnRte | Ramp down rate as a percentage of max current.
4 |  | EmgRmpUpRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Emergency Ramp Up Rate | Emergency ramp up rate as a percentage of max current.
5 |  | EmgRmpDnRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Emergency Ramp Down Rate | Emergency ramp down rate as a percentage of max current.
6 |  | ConnRmpUpRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Connect Ramp Up Rate | Connect ramp up rate as a percentage of max current.
7 |  | ConnRmpDnRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Connect Ramp Down Rate | Connect ramp down rate as a percentage of max current.
8 |  | AGra |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Default Ramp Rate | Ramp rate specified in percent of max current.
9 |  | Rmp_SF |  |  | sunssf | [6 empty] | Ramp Rate Scale Factor | Ramp Rate Scale Factor

## 160
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | mppt |  |  | group | [6 empty] | Multiple MPPT Inverter Extension Model
0 |  | ID | 160 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf | [6 empty] | Current Scale Factor
3 |  | DCV_SF |  |  | sunssf | [6 empty] | Voltage Scale Factor
4 |  | DCW_SF |  |  | sunssf | [6 empty] | Power Scale Factor
5 |  | DCWH_SF |  |  | sunssf | [6 empty] | Energy Scale Factor
6 |  | Evt |  |  | bitfield32 | [6 empty] | Global Events
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | RESERVED_16 | 16
|  | RESERVED_17 | 17
|  | RESERVED_18 | 18
|  | RESERVED_19 | 19
|  | TEST_FAILED | 20
|  | INPUT_UNDER_VOLTAGE | 21
|  | INPUT_OVER_CURRENT | 22
8 |  | N |  |  | count | [6 empty] | Number of Modules
9 |  | TmsPer |  |  | uint16 | [6 empty] | Timestamp Period
|  | mppt.module |  | 0 | group
| 0 | ID |  |  | uint16 | [6 empty] | Input ID
| 1 | IDStr |  |  | string | 8 | [5 empty] | Input ID String
| 9 | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Current
| 10 | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage
| 11 | DCW |  |  | uint16 |  | DCW_SF | W |  |  |  | DC Power
| 12 | DCWH |  |  | acc32 |  | DCWH_SF | Wh |  |  |  | Lifetime Energy
| 14 | Tms |  |  | uint32 |  |  | Secs |  |  |  | Timestamp
| 16 | Tmp |  |  | int16 |  |  | C |  |  |  | Temperature
| 17 | DCSt |  |  | enum16 | [6 empty] | Operating State
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
|  | TEST | 9
|  | RESERVED_10 | 10
| 18 | DCEvt |  |  | bitfield32 | [6 empty] | Module Events
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | RESERVED_16 | 16
|  | RESERVED_17 | 17
|  | RESERVED_18 | 18
|  | RESERVED_19 | 19
|  | TEST_FAILED | 20
|  | INPUT_UNDER_VOLTAGE | 21
|  | INPUT_OVER_CURRENT | 22

## 201
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_an_or_ab |  |  | group | [6 empty] | Meter (Single Phase) single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
0 |  | ID | 201 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  |  |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  |  |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases) | Conditional AN connection
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage AN | Phase Voltage AN | Conditional AN connection
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PPVphAB |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB | Conditional AB connection
13 |  | PPVphBC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | Power_Failure | 2
|  | Under_Voltage | 3
|  | Low_PF | 4
|  | Over_Current | 5
|  | Over_Voltage | 6
|  | Missing_Sensor | 7
|  | OEM01 | 16
|  | OEM02 | 17
|  | OEM03 | 18
|  | OEM04 | 19
|  | OEM05 | 20
|  | OEM06 | 21
|  | OEM07 | 22
|  | OEM08 | 23
|  | OEM09 | 24
|  | OEM10 | 25
|  | OEM11 | 26
|  | OEM12 | 27
|  | OEM13 | 28
|  | OEM14 | 29
|  | OEM15 | 30

## 202
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_abn |  |  | group | [6 empty] | split single phase (ABN) meter
0 |  | ID | 202 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  |  |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PhVphAB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AB | Phase Voltage AB
13 |  | PhVphBC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PhVphCA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 203
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_abcn |  |  | group | [6 empty] | wye-connect three phase (abcn) meter
0 |  | ID | 203 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PhVphAB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AB | Phase Voltage AB
13 |  | PhVphBC |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BC | Phase Voltage BC
14 |  | PhVphCA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 204
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_abc |  |  | group | [6 empty] | delta-connect three phase (abc) meter
0 |  | ID | 204 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PhVphAB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AB | Phase Voltage AB
13 |  | PhVphBC |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BC | Phase Voltage BC
14 |  | PhVphCA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 211
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_an_or_ab_float |  |  | group | [6 empty] | single phase (AN or AB) meter
0 |  | ID | 211 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  |  |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  |  |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 212
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_abn_float |  |  | group | [6 empty] | split single phase (ABN) meter
0 |  | ID | 212 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 213
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_abcn_float |  |  | group | [6 empty] | wye-connect three phase (abcn) meter
0 |  | ID | 213 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  | M |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 214
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_abc_float |  |  | group | [6 empty] | delta-connect three phase (abc) meter
0 |  | ID | 214 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 220
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ac_meter_secure |  |  | group | [6 empty] | Secure AC Meter Selected Readings | Include this model for secure metering
0 |  | ID | 220 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
4 |  | PhV |  |  | int16 |  | V_SF | V |  |  |  | Voltage | Average phase or line voltage
5 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
6 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
7 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
8 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
9 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
10 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
11 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
12 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
13 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
14 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
15 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
16 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
18 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
20 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
21 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
23 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
25 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
26 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
28 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
30 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
32 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
34 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
35 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | Power_Failure | 2
|  | Under_Voltage | 3
|  | Low_PF | 4
|  | Over_Current | 5
|  | Over_Voltage | 6
|  | Missing_Sensor | 7
|  | OEM01 | 16
|  | OEM02 | 17
|  | OEM03 | 18
|  | OEM04 | 19
|  | OEM05 | 20
|  | OEM06 | 21
|  | OEM07 | 22
|  | OEM08 | 23
|  | OEM09 | 24
|  | OEM10 | 25
|  | OEM11 | 26
|  | OEM12 | 27
|  | OEM13 | 28
|  | OEM14 | 29
|  | OEM15 | 30
37 |  | Rsrvd |  |  | pad |  |  |  |  | M
38 |  | Ts |  |  | uint32 |  |  |  |  | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
40 |  | Ms |  |  | uint16 |  |  |  |  | M |  | Milliseconds | Millisecond counter 0-999
41 |  | Seq |  |  | uint16 |  |  |  |  | M |  | Sequence | Sequence number of request | Shall be advanced for each request
42 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature | For future proof
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
43 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
|  | ac_meter_secure.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  |  | M

## 302
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | irradiance |  |  | group | [6 empty] | Irradiance Model | Include to support various irradiance measurements
0 |  | ID | 302 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | irradiance.repeating |  | 0 | group
| 0 | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance
| 1 | POAI |  |  | uint16 |  |  | W/m2 |  |  |  | POAI | Plane-of-Array Irradiance
| 2 | DFI |  |  | uint16 |  |  | W/m2 |  |  |  | DFI | Diffuse Irradiance
| 3 | DNI |  |  | uint16 |  |  | W/m2 |  |  |  | DNI | Direct Normal Irradiance
| 4 | OTI |  |  | uint16 |  |  | W/m2 |  |  |  | OTI | Other Irradiance

## 303
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | bom_temp |  |  | group | [6 empty] | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
0 |  | ID | 303 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | bom_temp.temp |  | 0 | group
| 0 | TmpBOM |  |  | int16 |  | -1 | C |  | M |  | Temp | Back of module temperature measurement

## 304
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | inclinometer |  |  | group | [6 empty] | Inclinometer Model | Include to support orientation measurements
0 |  | ID | 304 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | inclinometer.incl |  | 0 | group
| 0 | Inclx |  |  | int32 |  | -2 | Degrees |  | M |  | X | X-Axis inclination
| 2 | Incly |  |  | int32 |  | -2 | Degrees |  |  |  | Y | Y-Axis inclination
| 4 | Inclz |  |  | int32 |  | -2 | Degrees |  |  |  | Z | Z-Axis inclination

## 305
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | location |  |  | group | [6 empty] | GPS | Include to support location measurements
0 |  | ID | 305 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Tm |  |  | string | 6 |  | hhmmss.sssZ |  |  |  | Tm | UTC 24 hour time stamp to millisecond hhmmss.sssZ format
8 |  | Date |  |  | string | 4 |  | YYYYMMDD |  |  |  | Date | UTC Date string YYYYMMDD format
12 |  | Loc |  |  | string | 20 |  | text |  |  |  | Location | Location string (40 chars max)
32 |  | Lat |  |  | int32 |  | -7 | Degrees |  |  |  | Lat | Latitude with seven degrees of precision
34 |  | Long |  |  | int32 |  | -7 | Degrees |  |  |  | Long | Longitude with seven degrees of precision
36 |  | Alt |  |  | int32 |  |  | meters |  |  |  | Altitude | Altitude measurement in meters

## 306
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ref_point |  |  | group | [6 empty] | Reference Point Model | Include to support a standard reference point
0 |  | ID | 306 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance
3 |  | A |  |  | uint16 |  |  | W/m2 |  |  |  | Amps | Current measurement at reference point
4 |  | V |  |  | uint16 |  |  | W/m2 |  |  |  | Voltage | Voltage measurement at reference point
5 |  | Tmp |  |  | uint16 |  |  | W/m2 |  |  |  | Temperature | Temperature measurement at reference point

## 307
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | base_met |  |  | group | [6 empty] | Base Met | Base Meteorological Model
0 |  | ID | 307 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | TmpAmb |  |  | int16 |  | -1 | C |  |  |  | Ambient Temperature
3 |  | RH |  |  | int16 |  |  | Pct |  |  |  | Relative Humidity
4 |  | Pres |  |  | int16 |  |  | HPa |  |  |  | Barometric Pressure
5 |  | WndSpd |  |  | int16 |  |  | mps |  |  |  | Wind Speed
6 |  | WndDir |  |  | int16 |  |  | deg |  |  |  | Wind Direction
7 |  | Rain |  |  | int16 |  |  | mm |  |  |  | Rainfall
8 |  | Snw |  |  | int16 |  |  | mm |  |  |  | Snow Depth
9 |  | PPT |  |  | int16 | [6 empty] | Precipitation Type | Precipitation Type (WMO 4680 SYNOP code reference)
10 |  | ElecFld |  |  | int16 |  |  | Vm |  |  |  | Electric Field
11 |  | SurWet |  |  | int16 |  |  | kO |  |  |  | Surface Wetness
12 |  | SoilWet |  |  | int16 |  |  | Pct |  |  |  | Soil Wetness

## 308
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | mini_met |  |  | group | [6 empty] | Mini Met Model | Include to support a few basic measurements
0 |  | ID | 308 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance
3 |  | TmpBOM |  |  | int16 |  | -1 | C |  |  |  | Temp | Back of module temperature measurement
4 |  | TmpAmb |  |  | int16 |  | -1 | C |  |  |  | Ambient Temperature
5 |  | WndSpd |  |  | uint16 |  |  | m/s |  |  |  | Wind Speed

## 401
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | string_combiner_current |  |  | group | [6 empty] | String Combiner (Current) | A basic string combiner
0 |  | ID | 401 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCAMax |  |  | uint16 |  | DCA_SF | A |  | M |  | Rating | Maximum DC Current Rating
6 |  | N |  |  | count |  |  |  |  | M |  | N | Number of Inputs
7 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
9 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
11 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
12 |  | DCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
14 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
15 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
|  | string_combiner_current.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | InEvtVnd |  |  | bitfield32 | [6 empty] | Input Event Vendor | String Input Vendor Event Flags
| 5 | InDCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours

## 402
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | string_combiner_advanced |  |  | group | [6 empty] | String Combiner (Advanced) | An advanced string combiner
0 |  | ID | 402 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCW_SF |  |  | sunssf | [7 empty] | Power scale factor
6 |  | DCWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Energy scale factor
7 |  | DCAMax |  |  | uint16 |  |  | A |  |  |  | Rating | Maximum DC Current Rating
8 |  | N |  |  | count | [6 empty] | N | Number of Inputs
9 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
11 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
13 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
14 |  | DCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
16 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
17 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
18 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | Watts | Output power
19 |  | DCPR |  |  | uint16 |  |  | Pct |  |  |  | PR | DC Performance ratio value
20 |  | DCWh |  |  | uint32 |  | DCWh_SF | Wh |  | M |  | Watt-hours | Output energy
|  | string_combiner_advanced.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
| 5 | InDCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours
| 8 | InDCV |  |  | uint16 |  | DCV_SF | V |  |  |  | Voltage | String Input Voltage
| 9 | InDCW |  |  | int16 |  | DCWh_SF | W |  |  |  | Watts | String Input Power
| 10 | InDCWh |  |  | uint32 |  |  | Wh |  |  |  | Watt-hours | String Input Energy
| 12 | InDCPR |  |  | uint16 |  |  | Pct |  |  |  | PR | String Performance Ratio
| 13 | InN |  |  | uint16 | [6 empty] | N | Number of modules in this input string

## 403
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | string_combiner_current_input |  |  | group | [6 empty] | String Combiner (Current) | A basic string combiner model
0 |  | ID | 403 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCAMax |  |  | uint16 |  | DCA_SF | A |  | M |  | Rating | Maximum DC Current Rating
6 |  | N |  |  | count |  |  |  |  | M |  | N | Number of Inputs
7 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
9 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
11 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
12 |  | DCAhr |  |  | acc32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
14 |  | DCV |  |  | int16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
15 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
16 |  | InDCA_SF |  |  | sunssf | [7 empty] | Current scale factor for inputs
17 |  | InDCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor for inputs
|  | string_combiner_current_input.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | InEvtVnd |  |  | bitfield32 | [6 empty] | Input Event Vendor | String Input Vendor Event Flags
| 5 | InDCA |  |  | int16 |  | InDCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | acc32 |  | InDCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours

## 404
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | string_combiner_advanced_inputs |  |  | group | [6 empty] | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements
0 |  | ID | 404 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCW_SF |  |  | sunssf | [7 empty] | Power scale factor
6 |  | DCWh_SF |  |  | sunssf | [7 empty] | Energy scale factor
7 |  | DCAMax |  |  | uint16 |  | DCA_SF | A |  | M |  | Rating | Maximum DC Current Rating
8 |  | N |  |  | count |  |  |  |  | M |  | N | Number of Inputs
9 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
11 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
13 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
14 |  | DCAhr |  |  | acc32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
16 |  | DCV |  |  | int16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
17 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
18 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | Watts | Output power
19 |  | DCPR |  |  | int16 |  |  | Pct |  |  |  | PR | DC Performance ratio value
20 |  | DCWh |  |  | acc32 |  | DCWh_SF | Wh |  |  |  | Watt-hours | Output energy
22 |  | InDCA_SF |  |  | sunssf | [7 empty] | Current scale factor for inputs
23 |  | InDCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor for inputs
24 |  | InDCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor for inputs
25 |  | InDCW_SF |  |  | sunssf | [7 empty] | Power scale factor for inputs
26 |  | InDCWh_SF |  |  | sunssf | [7 empty] | Energy scale factor for inputs
|  | string_combiner_advanced_inputs.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | InEvtVnd |  |  | bitfield32 | [6 empty] | Input Event Vendor | String Input Vendor Event Flags
| 5 | InDCA |  |  | int16 |  | InDCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | acc32 |  | InDCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours
| 8 | InDCV |  |  | int16 |  | InDCV_SF | V |  |  |  | Voltage | String Input Voltage
| 9 | InDCW |  |  | int16 |  | InDCW_SF | W |  |  |  | Watts | String Input Power
| 10 | InDCWh |  |  | acc32 |  | InDCWh_SF | Wh |  |  |  | Watt-hours | String Input Energy
| 12 | InDCPR |  |  | uint16 |  |  | Pct |  |  |  | PR | String Performance Ratio
| 13 | InN |  |  | uint16 | [6 empty] | N | Number of modules in this input string

## 501
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | solar_module_float |  |  | group | [6 empty] | Solar Module | A solar module model supporting DC-DC converter
0 |  | ID | 501 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Stat |  |  | enum16 |  |  |  |  | M |  | Status | Enumerated value. Module Status Code
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
|  | TEST | 9
|  | OTHER | 10
3 |  | StatVend |  |  | enum16 | [6 empty] | Vendor Status | Module Vendor Status Code
4 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Bitmask value. Module Event Flags
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | RESERVED_5 | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMPERATURE | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMPERATURE | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | THEFT_DETECTION | 16
|  | OUTPUT_OVER_CURRENT | 17
|  | OUTPUT_OVER_VOLTAGE | 18
|  | OUTPUT_UNDER_VOLTAGE | 19
|  | TEST_FAILED | 20
6 |  | EvtVend |  |  | bitfield32 | [6 empty] | Vendor Module Event Flags | Vendor specific flags
8 |  | Ctl |  |  | enum16 |  |  |  | RW |  |  | Control | Module Control
9 |  | CtlVend |  |  | enum32 |  |  |  | RW |  |  | Vendor Control | Vendor Module Control
11 |  | CtlVal |  |  | int32 |  |  |  | RW |  |  | Control Value | Module Control Value
13 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Timestamp | Time in seconds since 2000 epoch
15 |  | OutA |  |  | float32 |  |  | A |  |  |  | Output Current | Output Current
17 |  | OutV |  |  | float32 |  |  | V |  |  |  | Output Voltage | Output Voltage
19 |  | OutWh |  |  | float32 |  |  | Wh |  |  |  | Output Energy | Output Energy
21 |  | OutW |  |  | float32 |  |  | W |  |  |  | Output Power | Output Power
23 |  | Tmp |  |  | float32 |  |  | C |  |  |  | Temp | Module Temperature
25 |  | InA |  |  | float32 |  |  | A |  |  |  | Input Current | Input Current
27 |  | InV |  |  | float32 |  |  | V |  |  |  | Input Voltage | Input Voltage
29 |  | InWh |  |  | float32 |  |  | Wh |  |  |  | Input Energy | Input Energy
31 |  | InW |  |  | float32 |  |  | W |  |  |  | Input Power | Input Power

## 502
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | solar_module |  |  | group | [6 empty] | Solar Module | A solar module model supporting DC-DC converter
0 |  | ID | 502 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A_SF |  |  | sunssf | [7 empty] | Current scale factor
3 |  | V_SF |  |  | sunssf | [7 empty] | Voltage scale factor
4 |  | W_SF |  |  | sunssf | [7 empty] | Power scale factor
5 |  | Wh_SF |  |  | sunssf | [7 empty] | Energy scale factor
6 |  | Stat |  |  | enum16 |  |  |  |  | M |  | Status | Enumerated value. Module Status Code
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
|  | TEST | 9
|  | OTHER | 10
7 |  | StatVend |  |  | enum16 | [6 empty] | Vendor Status | Module Vendor Status Code
8 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Bitmask value. Module Event Flags
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | RESERVED_5 | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMPERATURE | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMPERATURE | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | THEFT_DETECTION | 16
|  | OUTPUT_OVER_CURRENT | 17
|  | OUTPUT_OVER_VOLTAGE | 18
|  | OUTPUT_UNDER_VOLTAGE | 19
|  | TEST_FAILED | 20
10 |  | EvtVend |  |  | bitfield32 | [6 empty] | Vendor Module Event Flags | Vendor specific flags
12 |  | Ctl |  |  | enum16 |  |  |  | RW |  |  | Control | Module Control
13 |  | CtlVend |  |  | enum32 |  |  |  | RW |  |  | Vendor Control | Vendor Module Control
15 |  | CtlVal |  |  | int32 |  |  |  | RW |  |  | Control Value | Module Control Value
17 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Timestamp | Time in seconds since 2000 epoch
19 |  | OutA |  |  | int16 |  | A_SF | A |  |  |  | Output Current | Output Current
20 |  | OutV |  |  | int16 |  | V_SF | V |  |  |  | Output Voltage | Output Voltage
21 |  | OutWh |  |  | acc32 |  | Wh_SF | Wh |  |  |  | Output Energy | Output Energy
23 |  | OutPw |  |  | int16 |  | W_SF | W |  |  |  | Output Power | Output Power
24 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Module Temperature
25 |  | InA |  |  | int16 |  | A_SF | A |  |  |  | Input Current | Input Current
26 |  | InV |  |  | int16 |  | V_SF | V |  |  |  | Input Voltage | Input Voltage
27 |  | InWh |  |  | acc32 |  | Wh_SF | Wh |  |  |  | Input Energy | Input Energy
29 |  | InW |  |  | int16 |  | W_SF | W |  |  |  | Input Power | Input Power

## 601
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | tracker_controller |  |  | group | [6 empty] | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers
0 |  | ID | 601 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 8 | [5 empty] | Controller | Descriptive name for this control unit
10 |  | Typ |  |  | enum16 |  |  |  |  | M |  | Type | Type of tracker
|  | Unknown | 0
|  | Fixed | 1
|  | Horizontal | 2
|  | Tilted | 3
|  | Azimuth | 4
|  | Dual | 5
|  | Other | 99
11 |  | DtLoc |  |  | string | 5 |  | YYYYMMDD |  |  |  | Date | Local date in YYYYMMDD format
16 |  | TmLoc |  |  | string | 3 |  | hhmmss |  |  |  | Time | 24 hour local time stamp to second
19 |  | Day |  |  | uint16 | [6 empty] | Day | Number of the day in the year (1-366)
20 |  | GlblElCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Elevation | Global manual override target position of elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
22 |  | GlblAzCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Azimuth | Global manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
24 |  | GlblCtl |  |  | enum16 |  |  |  | RW |  |  | Global Mode | Global Control register operates on all trackers. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete. | The global controls all trackers
|  | Automatic | 0
|  | Manual | 1
|  | Calibrate | 2
25 |  | GlblAlm |  |  | bitfield16 | [6 empty] | Global Alarm | Global tracker alarm conditions | Combined tracker alarm conditions. See individual trackers for alarms
|  | SetPoint | 0
|  | ObsEl | 1
|  | ObsAz | 2
26 |  | Dgr_SF |  |  | sunssf |  |  |  |  | M |  | SF | Scale Factor for targets and position measurements in degrees
27 |  | N |  |  | uint16 |  |  |  |  | M |  | Trackers | Number of trackers being controlled. Size of repeating block.
|  | tracker_controller.tracker |  | 0 | group
| 0 | Id |  |  | string | 8 | [5 empty] | Tracker | Descriptive name for this tracker unit
| 8 | ElTrgt |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Target Elevation | Auto target elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
| 10 | AzTrgt |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Target Azimuth | Auto target azimuth in degrees from true north towards east. Unimplemented for single axis horizontal tracker type
| 12 | ElPos |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Elevation | Actual elevation position in degrees from horizontal. Unimplemented for single axis azimuth tracker type
| 14 | AzPos |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Azimuth | Actual azimuth position in degrees from true north towards east. Unimplemented for single axis horizontal tracker type
| 16 | ElCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Elevation | Manual override target position of elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
| 18 | AzCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Azimuth | Manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
| 20 | Ctl |  |  | enum16 |  |  |  | RW |  |  | Mode | Control register. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete.
|  | Automatic | 0
|  | Manual | 1
|  | Calibrate | 2
| 21 | Alm |  |  | bitfield16 | [6 empty] | Alarm | Tracker alarm conditions
|  | SetPoint | 0
|  | ObsEl | 1
|  | ObsAz | 2

## 701
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERMeasureAC |  |  | group | [6 empty] | DER AC Measurement | DER AC measurement model.
0 |  | ID | 701 |  | uint16 |  |  |  |  | M | S | Model ID | DER AC measurement model ID. |  | IEEE 1547-2018
1 |  | L | 153 |  | uint16 |  |  |  |  | M | S | Model Length | DER AC measurement model length. |  | IEEE 1547-2018
Wiring Type
2 |  | ACType |  |  | enum16 |  |  |  |  | M |  | AC Wiring Type | AC wiring type.
|  | SINGLE_PHASE | 0 | [8 empty] | Single Phase
|  | SPLIT_PHASE | 1 | [8 empty] | Split Phase
|  | THREE_PHASE | 2 | [8 empty] | Three Phase
Operating State
3 |  | St |  |  | enum16 | [6 empty] | Operating State | Operating state of the DER. |  | IEEE 1547-2018
|  | OFF | 0 | [8 empty] | Off
|  | ON | 1 | [8 empty] | On
Inverter State
4 |  | InvSt |  |  | enum16 | [6 empty] | Inverter State | Enumerated value. Inverter state.
|  | OFF | 0
|  | SLEEPING | 1
|  | STARTING | 2
|  | RUNNING | 3
|  | THROTTLED | 4
|  | SHUTTING_DOWN | 5
|  | FAULT | 6
|  | STANDBY | 7
Grid Connection State
5 |  | ConnSt |  |  | enum16 | [6 empty] | Grid Connection State | Grid connection state of the DER. |  | IEEE 1547-2018
|  | DISCONNECTED | 0 | [8 empty] | Disconnected | Disconnected from the grid.
|  | CONNECTED | 1 | [8 empty] | Connected | Connected to the grid.
Alarms
6 |  | Alrm |  |  | bitfield32 | [6 empty] | Alarm Bitfield | Active alarms for the DER. |  | IEEE 1547-2018
|  | GROUND_FAULT | 0 | [8 empty] | Ground Fault
|  | DC_OVER_VOLT | 1 | [8 empty] | DC Over Voltage
|  | AC_DISCONNECT | 2 | [8 empty] | AC Disconnect Open
|  | DC_DISCONNECT | 3 | [8 empty] | DC Disconnect Open
|  | GRID_DISCONNECT | 4 | [8 empty] | Grid Disconnect
|  | CABINET_OPEN | 5 | [8 empty] | Cabinet Open
|  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual Shutdown
|  | OVER_TEMP | 7 | [8 empty] | Over Temperature
|  | OVER_FREQUENCY | 8 | [8 empty] | Frequency Above Limit
|  | UNDER_FREQUENCY | 9 | [8 empty] | Frequency Under Limit
|  | AC_OVER_VOLT | 10 | [8 empty] | AC Voltage Above Limit
|  | AC_UNDER_VOLT | 11 | [8 empty] | AC Voltage Under Limit
|  | BLOWN_STRING_FUSE | 12 | [8 empty] | Blown String Fuse On Input
|  | UNDER_TEMP | 13 | [8 empty] | Under Temperature
|  | MEMORY_LOSS | 14 | [8 empty] | Generic Memory Or Communication Error (Internal)
|  | HW_TEST_FAILURE | 15 | [8 empty] | Hardware Test Failure
|  | MANUFACTURER_ALRM | 16 | [8 empty] | Manufacturer Alarm | Manufacturer alarm, see ManAlrmInfo field for more information.
8 |  | DERMode |  |  | bitfield32 | [6 empty] | DER Operational Characteristics | Current operational characteristics of the DER.
|  | GRID_FOLLOWING | 0 | [8 empty] | Grid Following | The DER is operating as part of a larger grid.
|  | GRID_FORMING | 1 | [8 empty] | Grid Forming | The DER is providing the grid.
|  | PV_CLIPPED | 2 | [8 empty] | PV Output Clipped | The PV output is clipped.
Scale Factors
10 |  | W |  |  | int16 |  | W_SF | W |  |  |  | Active Power | Total active power. Active power is positive for DER generation and negative for absorption. |  | IEEE 1547-2018
11 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | Apparent Power | Total apparent power.
12 |  | Var |  |  | int16 |  | Var_SF | Var |  |  |  | Reactive Power | Total reactive power. |  | IEEE 1547-2018
13 |  | PF |  |  | int16 |  | PF_SF |  |  |  |  | Power Factor | Power factor. The sign of power factor should be the sign of active power.
14 |  | A |  |  | int16 |  | A_SF | A |  |  |  | Total AC Current | Total AC current.
15 |  | LLV |  |  | uint16 |  | V_SF | V |  |  |  | Voltage LL | Line to line AC voltage as an average of active phases. |  | IEEE 1547-2018
16 |  | LNV |  |  | uint16 |  | V_SF | V |  |  |  | Voltage LN | Line to neutral AC voltage as an average of active phases. |  | IEEE 1547-2018
17 |  | Hz |  |  | uint32 |  | Hz_SF | Hz |  |  |  | Frequency | AC frequency. |  | IEEE 1547-2018
19 |  | TotWhInj |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Energy Injected | Total active energy injected (Quadrants 1 & 4).
23 |  | TotWhAbs |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3).
27 |  | TotVarhInj |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2).
31 |  | TotVarhAbs |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4).
Temperatures
35 |  | TmpAmb |  |  | int16 |  | Tmp_SF | C |  |  |  | Ambient Temperature | Ambient temperature.
36 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  |  |  | Cabinet Temperature | Cabinet temperature.
37 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat sink temperature.
38 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer temperature.
39 |  | TmpSw |  |  | int16 |  | Tmp_SF | C |  |  |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature.
40 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other temperature.
L1
41 |  | WL1 |  |  | int16 |  | W_SF | W |  |  |  | Watts L1 | Active power L1.
42 |  | VAL1 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L1 | Apparent power L1.
43 |  | VarL1 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L1 | Reactive power L1.
44 |  | PFL1 |  |  | int16 |  | PF_SF |  |  |  |  | PF L1 | Power factor phase L1.
45 |  | AL1 |  |  | int16 |  | A_SF | A |  |  |  | Amps L1 | Current phase L1.
46 |  | VL1L2 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L1-L2 | Phase voltage L1-L2. |  | IEEE 1547-2018
47 |  | VL1 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L1-N | Phase voltage L1-N. |  | IEEE 1547-2018
48 |  | TotWhInjL1 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L1 | Total active energy injected L1.
52 |  | TotWhAbsL1 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L1 | Total active energy absorbed L1.
56 |  | TotVarhInjL1 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L1 | Total reactive energy injected L1.
60 |  | TotVarhAbsL1 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L1 | Total reactive energy absorbed L1.
L2
64 |  | WL2 |  |  | int16 |  | W_SF | W |  |  |  | Watts L2 | Active power L2.
65 |  | VAL2 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L2 | Apparent power L2.
66 |  | VarL2 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L2 | Reactive power L2.
67 |  | PFL2 |  |  | int16 |  | PF_SF |  |  |  |  | PF L2 | Power factor L2.
68 |  | AL2 |  |  | int16 |  | A_SF | A |  |  |  | Amps L2 | Current L2.
69 |  | VL2L3 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L2-L3 | Phase voltage L2-L3. |  | IEEE 1547-2018
70 |  | VL2 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L2-N | Phase voltage L2-N. |  | IEEE 1547-2018
71 |  | TotWhInjL2 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L2 | Total active energy injected L2.
75 |  | TotWhAbsL2 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L2 | Total active energy absorbed L2.
79 |  | TotVarhInjL2 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L2 | Total reactive energy injected L2.
83 |  | TotVarhAbsL2 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L2 | Total reactive energy absorbed L2.
L3
87 |  | WL3 |  |  | int16 |  | W_SF | W |  |  |  | Watts L3 | Active power L3.
88 |  | VAL3 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L3 | Apparent power L3.
89 |  | VarL3 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L3 | Reactive power L3.
90 |  | PFL3 |  |  | int16 |  | PF_SF |  |  |  |  | PF L3 | Power factor L3.
91 |  | AL3 |  |  | int16 |  | A_SF | A |  |  |  | Amps L3 | Current L3.
92 |  | VL3L1 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L3-L1 | Phase voltage L3-L1. |  | IEEE 1547-2018
93 |  | VL3 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L3-N | Phase voltage L3-N. |  | IEEE 1547-2018
94 |  | TotWhInjL3 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L3 | Total active energy injected L3.
98 |  | TotWhAbsL3 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L3 | Total active energy absorbed L3.
102 |  | TotVarhInjL3 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L3 | Total reactive energy injected L3.
106 |  | TotVarhAbsL3 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L3 | Total reactive energy absorbed L3.
Active Power Throttling
110 |  | ThrotPct |  |  | uint16 |  |  | Pct |  |  |  | Throttling In Pct | Throttling in pct of maximum active power.
111 |  | ThrotSrc |  |  | bitfield32 | [6 empty] | Throttle Source Information | Active throttling source.
|  | MAX_W | 0
|  | FIXED_W | 1
|  | FIXED_VAR | 2
|  | FIXED_PF | 3
|  | VOLT_VAR | 4
|  | FREQ_WATT | 5
|  | DYN_REACT_CURR | 6
|  | LVRT | 7
|  | HVRT | 8
|  | WATT_VAR | 9
|  | VOLT_WATT | 10
|  | SCHEDULED | 11
|  | LFRT | 12
|  | HFRT | 13
|  | DERATED | 14
Scale Factors
113 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor.
114 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
115 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor.
116 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
117 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
118 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor.
119 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
120 |  | TotWh_SF |  |  | sunssf | [5 empty] | S | Active Energy Scale Factor | Active energy scale factor.
121 |  | TotVarh_SF |  |  | sunssf | [5 empty] | S | Reactive Energy Scale Factor | Reactive energy scale factor.
122 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature scale factor.
Manufacturer Alarm Information
123 |  | MnAlrmInfo |  |  | string | 32 | [5 empty] | Manufacturer Alarm Info | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active.

## 702
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERCapacity |  |  | group | [6 empty] | DER Capacity | DER capacity model.
0 |  | ID | 702 |  | uint16 |  |  |  |  | M | S | Model ID | DER capacity model ID. |  | IEEE 1547-2018
1 |  | L | 50 |  | uint16 |  |  |  |  | M | S | Model Length | DER capacity model length. |  | IEEE 1547-2018
Nameplate Ratings - Specifies capacity ratings
2 |  | WMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power Max Rating | Maximum active power rating at unity power factor in watts. |  | IEEE 1547-2018
3 |  | WOvrExtRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power (Over-Excited) Rating | Active power rating at specified over-excited power factor in watts. |  | IEEE 1547-2018
4 |  | WOvrExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  | S | Specified Over-Excited PF | Specified over-excited power factor. |  | IEEE 1547-2018
5 |  | WUndExtRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power (Under-Excited) Rating | Active power rating at specified under-excited power factor in watts. |  | IEEE 1547-2018
6 |  | WUndExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  | S | Specified Under-Excited PF | Specified under-excited power factor. |  | IEEE 1547-2018
7 |  | VAMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Apparent Power Max Rating | Maximum apparent power rating in voltamperes. |  | IEEE 1547-2018
8 |  | VarMaxInjRtg |  |  | uint16 |  | Var_SF | Var |  |  | S | Reactive Power Injected Rating | Maximum injected reactive power rating in vars. |  | IEEE 1547-2018
9 |  | VarMaxAbsRtg |  |  | uint16 |  | Var_SF | Var |  |  | S | Reactive Power Absorbed Rating | Maximum absorbed reactive power rating in vars. |  | IEEE 1547-2018
10 |  | WChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Charge Rate Max Rating | Maximum active power charge rate in watts. |  | IEEE 1547-2018
11 |  | WDisChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Discharge Rate Max Rating | Maximum active power discharge rate in watts.
12 |  | VAChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Charge Rate Max VA Rating | Maximum apparent power charge rate in voltamperes. |  | IEEE 1547-2018
13 |  | VADisChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Discharge Rate Max VA Rating | Maximum apparent power discharge rate in voltamperes.
14 |  | VNomRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Nominal Rating | AC voltage nominal rating. | Voltages are LN for single phase DER (e.g. 120 V nominal), LL for split phase DER (e.g. 240 V nominal), and LL for three phase DER (e.g., 480 V nominal). | IEEE 1547-2018
15 |  | VMaxRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Max Rating | AC voltage maximum rating. | Voltages are LN for single phase DER (e.g. 120 V nominal), LL for split phase DER (e.g. 240 V nominal), and LL for three phase DER (e.g., 480 V nominal). | IEEE 1547-2018
16 |  | VMinRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Min Rating | AC voltage minimum rating. | Voltages are LN for single phase DER (e.g. 120 V nominal), LL for split phase DER (e.g. 240 V nominal), and LL for three phase DER (e.g., 480 V nominal). | IEEE 1547-2018
17 |  | AMaxRtg |  |  | uint16 |  | A_SF | A |  |  | S | AC Current Max Rating | AC current maximum rating in amps.
18 |  | PFOvrExtRtg |  |  | uint16 |  | PF_SF |  |  |  | S | PF Over-Excited Rating (Unused) | Unused. Please use WOvrExtRtgPF. | This point is duplicative of WOvrExtRtgPF.
19 |  | PFUndExtRtg |  |  | uint16 |  | PF_SF |  |  |  | S | PF Under-Excited Rating (Unused) | Unused. Please use WUndExtRtgPF. | This point is duplicative of WUndExtRtgPF.
20 |  | ReactSusceptRtg |  |  | uint16 |  | S_SF | S |  |  | S | Reactive Susceptance | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. |  | IEEE 1547-2018
21 |  | NorOpCatRtg |  |  | enum16 | [5 empty] | S | Normal Operating Category | Normal operating performance category as specified in IEEE 1547-2018. |  | IEEE 1547-2018
|  | CAT_A | 0 | [8 empty] | Category A
|  | CAT_B | 1 | [8 empty] | Category B
22 |  | AbnOpCatRtg |  |  | enum16 | [5 empty] | S | Abnormal Operating Category | Abnormal operating performance category as specified in IEEE 1547-2018. |  | IEEE 1547-2018
|  | CAT_1 | 0 | [8 empty] | Category I
|  | CAT_2 | 1 | [8 empty] | Category II
|  | CAT_3 | 2 | [8 empty] | Category III
23 |  | CtrlModes |  |  | bitfield32 | [5 empty] | S | Supported Control Modes | Supported control mode functions. |  | IEEE 1547-2018
|  | MAX_W | 0 | [8 empty] | Limit Maximum Active Power
|  | FIXED_W | 1 | [8 empty] | Fixed Active Power
|  | FIXED_VAR | 2 | [8 empty] | Fixed Reactive Power
|  | FIXED_PF | 3 | [8 empty] | Fixed Power Factor
|  | VOLT_VAR | 4 | [8 empty] | Volt-Var Function
|  | FREQ_WATT | 5 | [8 empty] | Freq-Watt Function
|  | DYN_REACT_CURR | 6 | [8 empty] | Dynamic Reactive Current Function
|  | LV_TRIP | 7 | [8 empty] | Low-Voltage Trip
|  | HV_TRIP | 8 | [8 empty] | High-Voltage Trip
|  | WATT_VAR | 9 | [8 empty] | Watt-Var Function
|  | VOLT_WATT | 10 | [8 empty] | Volt-Watt Function
|  | SCHEDULED | 11 | [8 empty] | Scheduling
|  | LF_TRIP | 12 | [8 empty] | Low-Frequency Trip
|  | HF_TRIP | 13 | [8 empty] | High-Frequency Trip
25 |  | IntIslandCatRtg |  |  | bitfield16 | [5 empty] | S | Intentional Island Categories | Intentional island categories.
|  | UNCATEGORIZED | 0 | [8 empty] | Uncategorized
|  | INT_ISL_CAPABLE | 1 | [8 empty] | Intentional Island-Capable
|  | BLACK_START_CAPABLE | 2 | [8 empty] | Black Start-Capable
|  | ISOCH_CAPABLE | 3 | [8 empty] | Isochronous-Capable
Settings - Used to adjust nameplate ratings
26 |  | WMax |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power Max Setting | Maximum active power setting used to adjust maximum active power setting.
27 |  | WMaxOvrExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Over-Excited) Setting | Active power setting at specified over-excited power factor in watts.
28 |  | WOvrExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Over-Excited PF | Specified over-excited power factor.
29 |  | WMaxUndExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Under-Excited) Setting | Active power setting at specified under-excited power factor in watts.
30 |  | WUndExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Under-Excited PF | Specified under-excited power factor.
31 |  | VAMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Apparent Power Max Setting | Maximum apparent power setting used to adjust maximum apparent power rating.
32 |  | VarMaxInj |  |  | uint16 |  | Var_SF | Var | RW |  |  | Reactive Power Injected Setting | Maximum injected reactive power setting used to adjust maximum injected reactive power rating.
33 |  | VarMaxAbs |  |  | uint16 |  | Var_SF | Var | RW |  |  | Reactive Power Absorbed Setting | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating.
34 |  | WChaRteMax |  |  | uint16 |  | W_SF | W | RW |  |  | Charge Rate Max Setting | Maximum active power charge rate setting used to adjust maximum active power charge rate rating.
35 |  | WDisChaRteMax |  |  | uint16 |  | W_SF | W | RW |  |  | Discharge Rate Max Setting | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating.
36 |  | VAChaRteMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Charge Rate Max VA Setting | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating.
37 |  | VADisChaRteMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Discharge Rate Max VA Setting | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating.
38 |  | VNom |  |  | uint16 |  | V_SF | V | RW |  |  | Nominal AC Voltage Setting | Nominal AC voltage setting. | Voltages are LN for single phase DER (e.g. 120 V nominal), LL for split phase DER (e.g. 240 V nominal), and LL for three phase DER (e.g., 480 V nominal).
39 |  | VMax |  |  | uint16 |  | V_SF | V | RW |  |  | AC Voltage Max Setting | AC voltage maximum setting used to adjust AC voltage maximum rating. | Voltages are LN for single phase DER (e.g. 120 V nominal), LL for split phase DER (e.g. 240 V nominal), and LL for three phase DER (e.g., 480 V nominal).
40 |  | VMin |  |  | uint16 |  | V_SF | V | RW |  |  | AC Voltage Min Setting | AC voltage minimum setting used to adjust AC voltage minimum rating. | Voltages are LN for single phase DER (e.g. 120 V nominal), LL for split phase DER (e.g. 240 V nominal), and LL for three phase DER (e.g., 480 V nominal).
41 |  | AMax |  |  | uint16 |  | A_SF | A | RW |  |  | AC Current Max Setting | Maximum AC current setting used to adjust maximum AC current rating.
42 |  | PFOvrExt |  |  | uint16 |  | PF_SF |  | RW |  |  | PF Over-Excited Setting (Unused) | Unused. Please use WOvrExtPF. | This point is duplicative of WOvrExtPF.
43 |  | PFUndExt |  |  | uint16 |  | PF_SF |  | RW |  |  | PF Under-Excited Setting (Unused) | Unused. Please use WUndExtPF. | This point is duplicative of WUndExtPF.
44 |  | IntIslandCat |  |  | bitfield16 |  |  |  | RW |  |  | Intentional Island Categories | Intentional island categories.
|  | UNCATEGORIZED | 0 | [8 empty] | Uncategorized
|  | INT_ISL_CAPABLE | 1 | [8 empty] | Intentional Island-Capable
|  | BLACK_START_CAPABLE | 2 | [8 empty] | Black Start-Capable
|  | ISOCH_CAPABLE | 3 | [8 empty] | Isochronous-Capable
Scale Factors
45 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
46 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
47 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor.
48 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
49 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
50 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor.
51 |  | S_SF |  |  | sunssf | [5 empty] | S | Susceptance Scale Factor | Susceptance scale factor.

## 703
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DEREnterService |  |  | group | [6 empty] | Enter Service | Enter service model.
0 |  | ID | 703 |  | uint16 |  |  |  |  | M | S | Model ID | Enter service model ID. |  | IEEE 1547-2018
1 |  | L | 17 |  | uint16 |  |  |  |  | M | S | Model Length | Enter service model length. |  | IEEE 1547-2018
2 |  | ES |  |  | enum16 |  |  |  | RW |  |  | Permit Enter Service | Permit enter service. |  | IEEE 1547-2018
|  | DISABLED | 0
|  | ENABLED | 1
3 |  | ESVHi |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage High | Enter service voltage high threshold as percent of normal voltage. |  | IEEE 1547-2018
4 |  | ESVLo |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage Low | Enter service voltage low threshold as percent of normal voltage. |  | IEEE 1547-2018
5 |  | ESHzHi |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency High | Enter service frequency high threshold. |  | IEEE 1547-2018
7 |  | ESHzLo |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency Low | Enter service frequency low threshold. |  | IEEE 1547-2018
9 |  | ESDlyTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Delay Time | Enter service delay time in seconds. |  | IEEE 1547-2018
11 |  | ESRndTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Random Delay | Enter service random delay in seconds.
13 |  | ESRmpTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Ramp Time | Enter service ramp time in seconds.
15 |  | ESDlyRemTms |  |  | uint32 |  |  | Secs |  |  |  | Enter Service Delay Remaining | Enter service delay time remaining in seconds.
17 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage percentage scale factor. |  | IEEE 1547-2018
18 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor. |  | IEEE 1547-2018

## 704
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERCtlAC |  |  | group | [6 empty] | DER AC Controls | DER AC controls model.
0 |  | ID | 704 |  | uint16 |  |  |  |  | M | S | Model ID | DER AC controls model ID. |  | IEEE 1547-2018
1 |  | L | 65 |  | uint16 |  |  |  |  | M | S | Model Length | DER AC controls model length. |  | IEEE 1547-2018
Set Power Factor (when injecting active power)
2 |  | PFWInjEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Inj) Enable | Power factor enable when injecting active power. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | PFWInjEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Power Factor Reversion Enable (W Inj) | Power factor reversion timer when injecting active power enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
4 |  | PFWInjRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Inj) | Power factor reversion timer when injecting active power.
6 |  | PFWInjRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Inj) | Power factor reversion time remaining when injecting active power.
Set Power Factor (when absorbing active power)
8 |  | PFWAbsEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Abs) Enable | Power factor enable when absorbing active power.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
9 |  | PFWAbsEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Power Factor Reversion Enable (W Abs) | Power factor reversion timer when absorbing active power enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
10 |  | PFWAbsRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Abs) | Power factor reversion timer when absorbing active power.
12 |  | PFWAbsRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Abs) | Power factor reversion time remaining when absorbing active power.
Limit Maximum Active Power Generation
14 |  | WMaxLimPctEna |  |  | enum16 |  |  |  | RW |  |  | Limit Max Power Pct Enable | Limit maximum active power percent enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
15 |  | WMaxLimPct |  |  | uint16 |  | WMaxLimPct_SF | Pct | RW |  |  | Limit Max Power Pct Setpoint | Limit maximum active power percent value. |  | IEEE 1547-2018
16 |  | WMaxLimPctRvrt |  |  | uint16 |  | WMaxLimPct_SF | Pct | RW |  |  | Reversion Limit Max Power Pct | Reversion limit maximum active power percent value.
17 |  | WMaxLimPctEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Limit Max Power Pct Enable | Reversion limit maximum active power percent value enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
18 |  | WMaxLimPctRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Limit Max Power Pct Reversion Time | Limit maximum active power percent reversion time.
20 |  | WMaxLimPctRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Limit Max Power Pct Rev Time Rem | Limit maximum active power percent reversion time remaining.
Set Active Power Level (may be negative for charging)
22 |  | WSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Enable | Set active power enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
23 |  | WSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Mode | Set active power mode.
|  | W_MAX_PCT | 0 | [8 empty] | Active Power As Max Percent | Active power setting is percentage of maximum active power.
|  | WATTS | 1 | [8 empty] | Active Power As Watts | Active power setting is in watts.
24 |  | WSet |  |  | int32 |  | WSet_SF | W | RW |  |  | Active Power Setpoint (W) | Active power setting value in watts.
26 |  | WSetRvrt |  |  | int32 |  | WSet_SF | W | RW |  |  | Reversion Active Power (W) | Reversion active power setting value in watts.
28 |  | WSetPct |  |  | int16 |  | WSetPct_SF | Pct | RW |  |  | Active Power Setpoint (Pct) | Active power setting value as percent.
29 |  | WSetPctRvrt |  |  | int16 |  | WSetPct_SF | Pct | RW |  |  | Reversion Active Power (Pct) | Reversion active power setting value as percent.
30 |  | WSetEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Active Power Enable | Reversion active power function enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
31 |  | WSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Active Power Reversion Time | Set active power reversion time.
33 |  | WSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Active Power Rev Time Rem | Set active power reversion time remaining.
Set Reactive Power Level
35 |  | VarSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Enable | Set reactive power enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
36 |  | VarSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Mode | Set reactive power mode. |  | IEEE 1547-2018
|  | W_MAX_PCT | 0 | [8 empty] | Reactive Power As Watt Max Pct | Reactive power setting is percent of maximum active power.
|  | VAR_MAX_PCT | 1 | [8 empty] | Reactive Power As Var Max Pct | Reactive power setting is percent of maximum reactive power.
|  | VAR_AVAIL_PCT | 2 | [8 empty] | Reactive Power As Var Avail Pct | Reactive power setting is percent of available reactive power.
|  | VA_MAX_PCT | 3 | [8 empty] | Reactive Power As VA Max Pct | Reactive power setting is percent of maximum apparent power.
|  | VARS | 4 | [8 empty] | Reactive Power As Vars | Reactive power is in vars.
37 |  | VarSetPri |  |  | enum16 |  |  |  | RW |  |  | Reactive Power Priority | Reactive power priority. |  | IEEE 1547-2018
|  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
|  | VENDOR | 2 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
38 |  | VarSet |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reactive Power Setpoint (Vars) | Reactive power setting value in vars.
40 |  | VarSetRvrt |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reversion Reactive Power (Vars) | Reversion reactive power setting value in vars.
42 |  | VarSetPct |  |  | int16 |  | VarSetPct_SF | Pct | RW |  |  | Reactive Power Setpoint (Pct) | Reactive power setting value as percent. |  | IEEE 1547-2018
43 |  | VarSetPctRvrt |  |  | int16 |  | VarSetPct_SF | Pct | RW |  |  | Reversion Reactive Power (Pct) | Reversion reactive power setting value as percent.
44 |  | VarSetEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Reactive Power Enable | Reversion reactive power function enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
45 |  | VarSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reactive Power Reversion Time | Set reactive power reversion time.
47 |  | VarSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reactive Power Rev Time Rem | Set reactive power reversion time remaining.
Ramp Rate
49 |  | WRmp |  |  | uint16 |  |  | %Max/Sec | RW |  |  | Normal Ramp Rate | Ramp rate for increases in active power during normal generation.
50 |  | WRmpRef |  |  | enum16 |  |  |  | RW |  |  | Normal Ramp Rate Reference | Ramp rate reference unit for increases in active power or current during normal generation.
|  | A_MAX | 0 | [8 empty] | Max Current Ramp | Ramp based on percent of max current per second.
|  | W_MAX | 1 | [8 empty] | Max Active Power Ramp | Ramp based on percent of max active power per second.
51 |  | VarRmp |  |  | uint16 |  |  | %Max/Sec | RW |  |  | Reactive Power Ramp Rate | Ramp rate based on max reactive power per second.
52 |  | AntiIslEna |  |  | enum16 |  |  |  | RW |  |  | Anti-Islanding Enable | Anti-islanding enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Anti-islanding is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Anti-islanding is enabled.
Scale Factors
53 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor. |  | IEEE 1547-2018
54 |  | WMaxLimPct_SF |  |  | sunssf | [5 empty] | S | Limit Max Power Scale Factor | Limit maximum power scale factor. |  | IEEE 1547-2018
55 |  | WSet_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
56 |  | WSetPct_SF |  |  | sunssf | [5 empty] | S | Active Power Pct Scale Factor | Active power pct scale factor.
57 |  | VarSet_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
58 |  | VarSetPct_SF |  |  | sunssf | [5 empty] | S | Reactive Power Pct Scale Factor | Reactive power pct scale factor. |  | IEEE 1547-2018
Power Factor Settings
|  | DERCtlAC.PFWInj |  |  | sync | [6 empty] | Power Factor (W Inj) | Power factor setpoint when injecting active power.
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Inj) | Power factor setpoint when injecting active power. |  | IEEE 1547-2018
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Inj) | Power factor excitation setpoint when injecting active power. |  | IEEE 1547-2018
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWInjRvrt |  |  | sync | [6 empty] | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Inj) | Reversion power factor excitation setpoint when injecting active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWAbs |  |  | sync | [6 empty] | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Abs) | Power factor excitation setpoint when absorbing active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWAbsRvrt |  |  | sync | [6 empty] | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Abs) | Reversion power factor excitation setpoint when absorbing active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.

## 705
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERVoltVar |  |  | group | [6 empty] | DER Volt-Var | DER Volt-Var model.
0 |  | ID | 705 |  | uint16 |  |  |  |  | M | S | Model ID | DER Volt-Var model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Volt-Var model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Volt-Var Module Enable | Volt-Var control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time.
9 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Remaining | Reversion time remaining in seconds.
11 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion Curve | Default curve after reversion timeout.
12 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points. |  | IEEE 1547-2018
13 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Var Scale Factor | Scale factor for curve var points. |  | IEEE 1547-2018
14 |  | RspTms_SF |  |  | sunssf |  |  |  |  | M | S | Open-Loop Scale Factor | Open loop response time scale factor. |  | IEEE 1547-2018
Stored Curve Sets - Number of curve sets contained in NCrv - The first set is read-only and indicates the current settings.
|  | DERVoltVar.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points. |  | IEEE 1547-2018
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference. |  | IEEE 1547-2018
|  | W_MAX_PCT | 0 | [8 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 1 | [8 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 2 | [8 empty] | Percent Available Vars
|  | VA_MAX_PCT | 3 | [8 empty] | Percent Max Apparent Power
| 2 | Pri |  |  | enum16 |  |  |  | RW |  |  | Power Priority | Power priority. |  | IEEE 1547-2018
|  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
|  | VENDOR | 2 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
| 3 | VRef |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Vref Adjustment | Vref adjustment as percentage of nominal voltage. |  | IEEE 1547-2018
| 4 | VRefAuto |  |  | uint16 |  | V_SF | VNomPct |  |  |  | Current Autonomous Vref | Autonomous vref value as a percentage of nominal voltage.
| 5 | VRefAutoEna |  |  | enum16 |  |  |  | RW |  |  | Autonomous Vref Enable | Enable autonomous vref. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled Flag | Disabled flag (Disabled = 0, Enabled = 1).
|  | ENABLED | 1 | [8 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
| 6 | VRefAutoTms |  |  | uint16 |  |  | Secs | RW |  |  | Auto Vref Time Constant | Autonomous vref time constant. |  | IEEE 1547-2018
| 7 | RspTms |  |  | uint32 |  | RspTms_SF | Secs | RW |  |  | Open Loop Response Time | Open loop response time. |  | IEEE 1547-2018
| 9 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored Curve Sets - Curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltVar.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
| 1 | Var |  |  | int16 |  | DeptRef_SF | DeptRef | RW |  |  | Reactive Power Point | Curve reactive power point as set in DeptRef point. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018

## 706
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERVoltWatt |  |  | group | [6 empty] | DER Volt-Watt | DER Volt-Watt model.
0 |  | ID | 706 |  | uint16 |  |  |  |  | M | S | Model ID | DER Volt-Watt model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Volt-Watt model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Volt-Watt Module Enable | Volt-Watt control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time.
9 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Remaining | Reversion time remaining in seconds.
11 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion Curve | Default curve after reversion timeout.
12 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points. |  | IEEE 1547-2018
13 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Watt Scale Factor | Scale factor for curve watt points. |  | IEEE 1547-2018
14 |  | RspTms_SF |  |  | sunssf |  |  |  |  | M | S | Open-Loop Scale Factor | Open loop response time scale factor. |  | IEEE 1547-2018
Stored curve sets - Number of curve sets contained in NCrv - The first set is read-only and indicates the current settings.
|  | DERVoltWatt.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points. |  | IEEE 1547-2018
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference. |  | IEEE 1547-2018
|  | W_MAX_PCT | 0
|  | W_AVAL_PCT | 1
| 2 | RspTms |  |  | uint32 |  | RspTms_SF | Secs | RW |  |  | Open Loop Response Time | Open loop response time. |  | IEEE 1547-2018
| 4 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltWatt.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
| 1 | W |  |  | int16 |  | DeptRef_SF | DeptRef | RW |  |  | Dependent Reference | Active power in percent of rated active power. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018

## 707
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERTripLV |  |  | group | [6 empty] | DER Trip LV | DER low voltage trip model.
0 |  | ID | 707 |  | uint16 |  |  |  |  | M | S | Model ID | DER low voltage trip model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER low voltage trip model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip LV Module Enable | DER low voltage trip control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points. |  | IEEE 1547-2018
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points. |  | IEEE 1547-2018
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripLV.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripLV.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve. |  | IEEE 1547-2018
|  | DERTripLV.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
|  | DERTripLV.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripLV.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripLV.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripLV.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 708
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERTripHV |  |  | group | [6 empty] | DER Trip HV | DER high voltage trip model.
0 |  | ID | 708 |  | uint16 |  |  |  |  | M | S | Model ID | DER high voltage trip model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER high voltage trip model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip HV Module Enable | DER high voltage trip control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points. |  | IEEE 1547-2018
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points. |  | IEEE 1547-2018
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripHV.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripHV.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve. |  | IEEE 1547-2018
|  | DERTripHV.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
|  | DERTripHV.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripHV.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripHV.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripHV.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | V |  |  | uint16 |  | V_SF | VNomPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 709
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERTripLF |  |  | group | [6 empty] | DER Trip LF | DER low frequency trip model.
0 |  | ID | 709 |  | uint16 |  |  |  |  | M | S | Model ID | DER low frequency trip model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER low frequency trip model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip LF Module Enable | DER low frequency trip control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | Hz_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Scale Factor | Scale factor for curve frequency points. |  | IEEE 1547-2018
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points. |  | IEEE 1547-2018
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripLF.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripLF.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve. |  | IEEE 1547-2018
|  | DERTripLF.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
|  | DERTripLF.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripLF.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripLF.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripLF.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 710
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERTripHF |  |  | group | [6 empty] | DER Trip HF | DER high frequency trip model.
0 |  | ID | 710 |  | uint16 |  |  |  |  | M | S | Model ID | DER high frequency trip model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER high frequency trip model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip HF Module Enable | DER high frequency trip control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | Hz_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Scale Factor | Scale factor for curve frequency points. |  | IEEE 1547-2018
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points. |  | IEEE 1547-2018
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripHF.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripHF.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve. |  | IEEE 1547-2018
|  | DERTripHF.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. | IEEE 1547-2018
|  | DERTripHF.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripHF.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripHF.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripHF.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 711
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERFreqDroop |  |  | group | [6 empty] | DER Frequency Droop | DER Frequency Droop model.
0 |  | ID | 711 |  | uint16 |  |  |  |  | M | S | Model ID | DER Frequency Droop model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Frequency Droop model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Frequency Droop Module Enable | DER Frequency-Watt (Frequency-Droop) control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCtlReq |  |  | uint16 |  |  |  | RW | M |  | Set Active Control Request | Set active control. 0 = No active control. |  | IEEE 1547-2018
4 |  | AdptCtlRslt |  |  | enum16 |  |  |  |  | M |  | Set Active Control Result | Result of last set active control operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Control update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Control update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Control update failed.
5 |  | NCtl |  |  | uint16 |  |  |  |  | M | S | Stored Control Count | Number of stored controls supported. |  | IEEE 1547-2018
6 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time.
8 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Left | Reversion time remaining in seconds.
10 |  | RvrtCtl |  |  | uint16 |  |  |  | RW |  |  | Reversion Control | Default control after reversion timeout.
11 |  | Db_SF |  |  | sunssf |  |  |  |  | M | S | Deadband Scale Factor | Deadband scale factor. |  | IEEE 1547-2018
12 |  | K_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Change Scale Factor | Frequency change scale factor. |  | IEEE 1547-2018
13 |  | RspTms_SF |  |  | sunssf |  |  |  |  | M | S | Open-Loop Scale Factor | Open loop response time scale factor. |  | IEEE 1547-2018
Stored control sets - Number of control sets contained in NCtl - The first set is read-only and indicates the current settings.
|  | DERFreqDroop.Ctl |  | NCtl | group | [6 empty] | Stored Controls | Stored control sets.
| 0 | DbOf |  |  | uint32 |  | Db_SF | Hz | RW | M |  | Over-Frequency Deadband | The deadband value for over-frequency conditions in Hz. |  | IEEE 1547-2018
| 2 | DbUf |  |  | uint32 |  | Db_SF | Hz | RW | M |  | Under-Frequency Deadband | The deadband value for under-frequency conditions in Hz. |  | IEEE 1547-2018
| 4 | KOf |  |  | uint16 |  | K_SF |  | RW | M |  | Over-Frequency Change Ratio | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. |  | IEEE 1547-2018
| 5 | KUf |  |  | uint16 |  | K_SF |  | RW | M |  | Under-Frequency Change Ratio | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. |  | IEEE 1547-2018
| 6 | RspTms |  |  | uint32 |  | RspTms_SF | Secs | RW | M |  | Open-Loop Response Time | The open-loop response time in seconds. |  | IEEE 1547-2018
| 8 | PMin |  |  | int16 |  |  | Pct | RW |  |  | Minimum Active Power | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control.
| 9 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Control Access | Control read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Control has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Control has read-only access.

## 712
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERWattVar |  |  | group | [6 empty] | DER Watt-Var | DER Watt-Var model.
0 |  | ID | 712 |  | uint16 |  |  |  |  | M | S | Model ID | DER Watt-Var model ID. |  | IEEE 1547-2018
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Watt-Var model length. |  | IEEE 1547-2018
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Watt-Var Module Enable | DER Watt-Var control enable. |  | IEEE 1547-2018
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Set Active Curve Request | Set active curve. 0 = No active curve. |  | IEEE 1547-2018
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Set Active Curve Result | Result of last set active curve operation. |  | IEEE 1547-2018
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  | IEEE 1547-2018
6 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  | IEEE 1547-2018
7 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time.
9 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Left | Reversion time remaining in seconds.
11 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion Curve | Default curve after reversion timeout.
12 |  | W_SF |  |  | sunssf |  |  |  |  | M | S | Active Power Scale Factor | Scale factor for curve active power points. |  | IEEE 1547-2018
13 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Var Scale Factor | Scale factor for curve var points. |  | IEEE 1547-2018
Stored curve sets - Number of curve sets contained in NCrv - The first set is read-only and indicates the current settings.
|  | DERWattVar.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points. |  | IEEE 1547-2018
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference. |  | IEEE 1547-2018
|  | W_MAX_PCT | 0 | [8 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 1 | [8 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 2 | [8 empty] | Percent Available Vars
|  | VA_MAX_PCT | 3 | [8 empty] | Percent Max Apparent Power
| 2 | Pri |  |  | enum16 |  |  |  | RW |  |  | Power Priority | Power priority. |  | IEEE 1547-2018
|  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
| 3 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  | IEEE 1547-2018
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERWattVar.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | W |  |  | int16 |  | W_SF | WMaxPct | RW |  |  | Active Power Point | Curve active power point as percentage. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. IEEE 1547 implementations must allow 0 values for all three load points. | IEEE 1547-2018
| 1 | Var |  |  | int16 |  | DeptRef_SF | VarPct | RW |  |  | Reactive Power Point | Curve reactive power point as set in DeptRef point. | Internal curve conformance checks should be conducted when AdptCrvReq is set to 1, not on point writes. IEEE 1547 implementations must allow 0 values for all three load points | IEEE 1547-2018

## 713
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERStorageCapacity |  |  | group | [6 empty] | DER Storage Capacity | DER storage capacity.
0 |  | ID | 713 |  | uint16 |  |  |  |  | M | S | Model ID | DER storage capacity model ID. |  | IEEE 1547-2018
1 |  | L | 7 |  | uint16 |  |  |  |  | M | S | Model Length | DER storage capacity model length. |  | IEEE 1547-2018
2 |  | WHRtg |  |  | uint16 |  | WH_SF | WH |  |  |  | Energy Rating | Energy rating of the DER storage.
3 |  | WHAvail |  |  | uint16 |  | WH_SF | WH |  |  |  | Energy Available | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH)
4 |  | SoC |  |  | uint16 |  | Pct_SF | Pct |  |  |  | State of Charge | State of charge of the DER storage. | SOC shall be fixed to 0% for DER without storage capabilities. | IEEE 1547-2018
5 |  | SoH |  |  | uint16 |  | Pct_SF | Pct |  |  |  | State of Health | State of health of the DER storage.
6 |  | Sta |  |  | enum16 | [6 empty] | Status | Storage status.
|  | OK | 0 | [8 empty] | OK | No warnings or errors pending.
|  | WARNING | 1 | [8 empty] | Warning | One or more warnings pending.
|  | ERROR | 2 | [8 empty] | Error | One or more errors pending.
7 |  | WH_SF |  |  | sunssf | [5 empty] | S | Energy Scale Factor | Scale factor for energy capacity.
8 |  | Pct_SF |  |  | sunssf | [5 empty] | S | Percent Scale Factor | Scale factor for percentage.

## 714
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERMeasureDC |  |  | group | [6 empty] | DER DC Measurement | DER DC measurement.
0 |  | ID | 714 |  | uint16 |  |  |  |  | M | S | Model ID | DER DC measurement model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER DC measurement model length.
DC General
2 |  | PrtAlrms |  |  | bitfield32 | [6 empty] | Port Alarms | Bitfield of ports with active alarms. Bit is 1 if port has an active alarm. Bit 0 is first port.
4 |  | NPrt |  |  | uint16 | [5 empty] | S | Number Of Ports | Number of DC ports.
5 |  | DCA |  |  | int16 |  | DCA_SF | A |  |  |  | DC Current | Total DC current for all ports.
6 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Power | Total DC power for all ports.
7 |  | DCWhInj |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Injected | Total cumulative DC energy injected for all ports.
11 |  | DCWhAbs |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Absorbed | Total cumulative DC energy absorbed for all ports.
15 |  | DCA_SF |  |  | sunssf | [5 empty] | S | DC Current Scale Factor | DC current scale factor.
16 |  | DCV_SF |  |  | sunssf | [5 empty] | S | DC Voltage Scale Factor | DC voltage scale factor.
17 |  | DCW_SF |  |  | sunssf | [5 empty] | S | DC Power Scale Factor | DC power scale factor.
18 |  | DCWH_SF |  |  | sunssf | [5 empty] | S | DC Energy Scale Factor | DC energy scale factor.
19 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature Scale Factor.
DC Port
|  | DERMeasureDC.Prt |  | NPrt | group
| 0 | PrtTyp |  |  | enum16 | [6 empty] | Port Type | Port type.
|  | PV | 0 | [8 empty] | Photovoltaic
|  | ESS | 1 | [8 empty] | Energy Storage System
|  | EV | 2 | [8 empty] | Electric Vehicle
|  | INJ | 3 | [8 empty] | Generic Injecting
|  | ABS | 4 | [8 empty] | Generic Absorbing
|  | BIDIR | 5 | [8 empty] | Generic Bidirectional
|  | DC_DC | 6 | [8 empty] | DC to DC
| 1 | ID |  |  | uint16 | [6 empty] | Port ID | Port ID.
| 2 | IDStr |  |  | string | 8 | [5 empty] | Port ID String | Port ID string.
| 10 | DCA |  |  | int16 |  | DCA_SF | A |  |  |  | DC Current | DC current for the port.
| 11 | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC voltage for the port.
| 12 | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Power | DC power for the port.
| 13 | DCWhInj |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Injected | Total cumulative DC energy injected for the port.
| 17 | DCWhAbs |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Absorbed | Total cumulative DC energy absorbed for the port.
| 21 | Tmp |  |  | int16 |  | Tmp_SF | C |  |  |  | DC Port Temperature | DC port temperature.
| 22 | DCSta |  |  | enum16 | [6 empty] | DC Port Status | DC port status.
|  | OFF | 0 | [8 empty] | Off
|  | ON | 1 | [8 empty] | On
|  | WARNING | 2 | [8 empty] | Warning
|  | ERROR | 3 | [8 empty] | Error
| 23 | DCAlrm |  |  | bitfield32 | [6 empty] | DC Port Alarm | DC port alarm.
|  | GROUND_FAULT | 0 | [8 empty] | Ground Fault
|  | INPUT_OVER_VOLTAGE | 1 | [8 empty] | Input Over Voltage
|  | DC_DISCONNECT | 3 | [8 empty] | DC Disconnect
|  | CABINET_OPEN | 5 | [8 empty] | Cabinet Open
|  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual Shutdown
|  | OVER_TEMP | 7 | [8 empty] | Over Temperature
|  | BLOWN_FUSE | 12 | [8 empty] | Blown Fuse
|  | UNDER_TEMP | 13 | [8 empty] | Under Temperature
|  | MEMORY_LOSS | 14 | [8 empty] | Memory Loss
|  | ARC_DETECTION | 15 | [8 empty] | Arc Detection
|  | RESERVED | 19 | [8 empty] | Reserved
|  | TEST_FAILED | 20 | [8 empty] | Test Failed
|  | INPUT_UNDER_VOLTAGE | 21 | [8 empty] | Under Voltage
|  | INPUT_OVER_CURRENT | 22 | [8 empty] | Over Current

## 715
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERCtl |  |  | group | [6 empty] | DERCtl | DER Control
0 |  | ID | 715 |  | uint16 |  |  |  |  | M | S | Model ID | DER control model ID.
1 |  | L | 7 |  | uint16 |  |  |  |  | M | S | Model Length | DER control model length.
DER Controls
2 |  | LocRemCtl |  |  | enum16 | [6 empty] | Control Mode | DER control mode. Enumeration.
|  | REMOTE | 0 | [8 empty] | Remote Control
|  | LOCAL | 1 | [8 empty] | Local Control | Local mode is required for manual/maintenance operations. Once invoked, it must be explicitly exited for the inverter to be controlled remotely.
3 |  | DERHb |  |  | uint32 | [6 empty] | DER Heartbeat | Value is incremented every second by the DER with periodic resets to zero.
5 |  | ControllerHb |  |  | uint32 |  |  |  | RW |  |  | Controller Heartbeat | Value is incremented every second by the controller with periodic resets to zero.
7 |  | AlarmReset |  |  | uint16 |  |  |  | RW |  |  | Alarm Reset | Used to reset any latched alarms. 1 = Reset.
8 |  | OpCtl |  |  | enum16 |  |  |  | RW |  |  | Set Operation | Commands to PCS. Enumerated value.
|  | STOP | 0 | [8 empty] | Stop the DER
|  | START | 1 | [8 empty] | Start the DER
|  | ENTER_STANDBY | 2 | [8 empty] | Enter Standby Mode
|  | EXIT_STANDBY | 3 | [8 empty] | Exit Standby Mode

## 801
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | storage |  |  | group | [6 empty] | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
0 |  | ID | 801 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DEPRECATED |  |  | enum16 |  |  |  |  | M |  | Deprecated Model | This model has been deprecated.

## 802
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | battery |  |  | group | [6 empty] | Battery Base Model
0 |  | ID | 802 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | AHRtg |  |  | uint16 |  | AHRtg_SF | Ah |  | M |  | Nameplate Charge Capacity | Nameplate charge capacity in amp-hours.
3 |  | WHRtg |  |  | uint16 |  | WHRtg_SF | Wh |  | M |  | Nameplate Energy Capacity | Nameplate energy capacity in DC watt-hours.
4 |  | WChaRteMax |  |  | uint16 |  | WChaDisChaMax_SF | W |  | M |  | Nameplate Max Charge Rate | Maximum rate of energy transfer into the storage device in DC watts.
5 |  | WDisChaRteMax |  |  | uint16 |  | WChaDisChaMax_SF | W |  | M |  | Nameplate Max Discharge Rate | Maximum rate of energy transfer out of the storage device in DC watts.
6 |  | DisChaRte |  |  | uint16 |  | DisChaRte_SF | %WHRtg |  |  |  | Self Discharge Rate | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
7 |  | SoCMax |  |  | uint16 |  | SoC_SF | %WHRtg |  |  |  | Nameplate Max SoC | Manufacturer maximum state of charge, expressed as a percentage.
8 |  | SoCMin |  |  | uint16 |  | SoC_SF | %WHRtg |  |  |  | Nameplate Min SoC | Manufacturer minimum state of charge, expressed as a percentage.
9 |  | SocRsvMax |  |  | uint16 |  | SoC_SF | %WHRtg | RW |  |  | Max Reserve Percent | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
10 |  | SoCRsvMin |  |  | uint16 |  | SoC_SF | %WHRtg | RW |  |  | Min Reserve Percent | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
11 |  | SoC |  |  | uint16 |  | SoC_SF | %WHRtg |  | M |  | State of Charge | State of charge, expressed as a percentage. | Measurement.
12 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | Depth of Discharge | Depth of discharge, expressed as a percentage. | Measurement.
13 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | State of Health | Percentage of battery life remaining.
14 |  | NCyc |  |  | uint32 | [6 empty] | Cycle Count | Number of cycles executed in the battery.
16 |  | ChaSt |  |  | enum16 | [6 empty] | Charge Status | Charge status of storage device. Enumeration.
|  | OFF | 1
|  | EMPTY | 2
|  | DISCHARGING | 3
|  | CHARGING | 4
|  | FULL | 5
|  | HOLDING | 6
|  | TESTING | 7
17 |  | LocRemCtl |  |  | enum16 |  |  |  |  | M |  | Control Mode | Battery control mode. Enumeration. | Maps to DRCC.LocRemCtl in IEC 61850.
|  | REMOTE | 0
|  | LOCAL | 1
18 |  | Hb |  |  | uint16 | [6 empty] | Battery Heartbeat | Value is incremented every second with periodic resets to zero.
19 |  | CtrlHb |  |  | uint16 |  |  |  | RW |  |  | Controller Heartbeat | Value is incremented every second with periodic resets to zero.
20 |  | AlmRst |  |  | uint16 |  |  |  | RW | M |  | Alarm Reset | Used to reset any latched alarms. 1 = Reset. | Battery should reset to 0 when reset is complete.
21 |  | Typ |  |  | enum16 |  |  |  |  | M |  | Battery Type | Type of battery. Enumeration. | Maps to DBAT.BatTyp in 61850.
|  | NOT APPLICABLE_UNKNOWN | 0
|  | LEAD_ACID | 1
|  | NICKEL_METAL_HYDRATE | 2
|  | NICKEL_CADMIUM | 3
|  | LITHIUM_ION | 4
|  | CARBON_ZINC | 5
|  | ZINC_CHLORIDE | 6
|  | ALKALINE | 7
|  | RECHARGEABLE_ALKALINE | 8
|  | SODIUM_SULFUR | 9
|  | FLOW | 10
|  | OTHER | 99
22 |  | State |  |  | enum16 |  |  |  |  | M |  | State of the Battery Bank | State of the battery bank. Enumeration. | Must be reconciled with State in IEC 61850.
|  | DISCONNECTED | 1
|  | INITIALIZING | 2
|  | CONNECTED | 3
|  | STANDBY | 4
|  | SOC PROTECTION | 5
|  | SUSPENDING | 6
|  | FAULT | 99
23 |  | StateVnd |  |  | enum16 | [6 empty] | Vendor Battery Bank State | Vendor specific battery bank state. Enumeration.
24 |  | WarrDt |  |  | uint32 | [6 empty] | Warranty Date | Date the device warranty expires. | Number of days since 1/1/2000.
26 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Battery Event 1 Bitfield | Alarms and warnings. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | CURRENT_IMBALANCE_WARNING | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_1 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
28 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Battery Event 2 Bitfield | Alarms and warnings. Bit flags. | Reserved for future use.
30 |  | EvtVnd1 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 1 | Vendor defined events.
32 |  | EvtVnd2 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 2 | Vendor defined events.
34 |  | V |  |  | uint16 |  | V_SF | V |  | M |  | External Battery Voltage | DC Bus Voltage. | Maps to ZBAT.V in IEC 61850.
35 |  | VMax |  |  | uint16 |  | V_SF | V |  |  |  | Max Battery Voltage | Instantaneous maximum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
36 |  | VMin |  |  | uint16 |  | V_SF | V |  |  |  | Min Battery Voltage | Instantaneous minimum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
37 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Max Cell Voltage | Maximum voltage for all cells in the bank. | Measurement.
38 |  | CellVMaxStr |  |  | uint16 | [6 empty] | Max Cell Voltage String | String containing the cell with maximum voltage.
39 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with maximum voltage.
40 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Min Cell Voltage | Minimum voltage for all cells in the bank. | Measurement.
41 |  | CellVMinStr |  |  | uint16 | [6 empty] | Min Cell Voltage String | String containing the cell with minimum voltage.
42 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with minimum voltage.
43 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average cell voltage for all cells in the bank. | Calculation based on measurements.
44 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Total DC Current | Total DC current flowing to/from the battery bank. | Measurement.
45 |  | AChaMax |  |  | uint16 |  | AMax_SF | A |  |  |  | Max Charge Current | Instantaneous maximum DC charge current. | Calculation which is always unsigned (i.e. magnitude only). If not implemented, must implement VMax and VMin.
46 |  | ADisChaMax |  |  | uint16 |  | AMax_SF | A |  |  |  | Max Discharge Current | Instantaneous maximum DC discharge current. | Calculation which is always unsigned (i.e. magnitude only). If not implemented, must implement VMax and VMin.
47 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Total Power | Total power flowing to/from the battery bank. | DC Measurement.
48 |  | ReqInvState |  |  | enum16 | [6 empty] | Inverter State Request | Request from battery to start or stop the inverter. Enumeration. | Used in special states such as manual battery charging.
|  | NO REQUEST | 0
|  | START | 1
|  | STOP | 2
49 |  | ReqW |  |  | int16 |  | W_SF | W |  |  |  | Battery Power Request | AC Power requested by battery. | Used in special states such as string balancing.
50 |  | SetOp |  |  | enum16 |  |  |  | RW | M |  | Set Operation | Instruct the battery bank to perform an operation such as connecting. Enumeration.
|  | CONNECT | 1
|  | DISCONNECT | 2
51 |  | SetInvState |  |  | enum16 |  |  |  | RW | M |  | Set Inverter State | Set the current state of the inverter. | Information needed by battery for some operations.
|  | INVERTER_STOPPED | 1
|  | INVERTER_STANDBY | 2
|  | INVERTER_STARTED | 3
52 |  | AHRtg_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for charge capacity.
53 |  | WHRtg_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for energy capacity.
54 |  | WChaDisChaMax_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for maximum charge and discharge rate.
55 |  | DisChaRte_SF |  |  | sunssf | [7 empty] | Scale factor for self discharge rate.
56 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for state of charge values.
57 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for depth of discharge.
58 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for state of health.
59 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for DC bus voltage.
60 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
61 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for DC current.
62 |  | AMax_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for instantaneous DC charge/discharge current.
63 |  | W_SF |  |  | sunssf | [7 empty] | Scale factor for AC power request.

## 803
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lithium_ion_bank |  |  | group | [6 empty] | Lithium-Ion Battery Bank Model
0 |  | ID | 803 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | NStr |  |  | uint16 |  |  |  |  | M |  | String Count | Number of strings in the bank.
3 |  | NStrCon |  |  | uint16 |  |  |  |  | M |  | Connected String Count | Number of strings with contactor closed.
4 |  | ModTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Module Temperature | Maximum temperature for all modules in the bank. | Measurement.
5 |  | ModTmpMaxStr |  |  | uint16 | [6 empty] | Max Module Temperature String | String containing the module with maximum temperature.
6 |  | ModTmpMaxMod |  |  | uint16 | [6 empty] | Max Module Temperature Module | Module with maximum temperature.
7 |  | ModTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Module Temperature | Minimum temperature for all modules in the bank. | Measurement.
8 |  | ModTmpMinStr |  |  | uint16 | [6 empty] | Min Module Temperature String | String containing the module with minimum temperature.
9 |  | ModTmpMinMod |  |  | uint16 | [6 empty] | Min Module Temperature Module | Module with minimum temperature.
10 |  | ModTmpAvg |  |  | int16 |  | ModTmp_SF | C |  |  |  | Average Module Temperature | Average temperature for all modules in the bank. | Calculation based on measurements.
11 |  | StrVMax |  |  | uint16 |  | V_SF | V |  |  |  | Max String Voltage | Maximum string voltage for all strings in the bank. | Measurement.
12 |  | StrVMaxStr |  |  | uint16 | [6 empty] | Max String Voltage String | String with maximum voltage.
13 |  | StrVMin |  |  | uint16 |  | V_SF | V |  |  |  | Min String Voltage | Minimum string voltage for all strings in the bank. | Measurement.
14 |  | StrVMinStr |  |  | uint16 | [6 empty] | Min String Voltage String | String with minimum voltage.
15 |  | StrVAvg |  |  | uint16 |  | V_SF | V |  |  |  | Average String Voltage | Average string voltage for all strings in the bank. | Calculation based on measurements.
16 |  | StrAMax |  |  | int16 |  | A_SF | A |  |  |  | Max String Current | Maximum current of any string in the bank. | Measurement.
17 |  | StrAMaxStr |  |  | uint16 | [6 empty] | Max String Current String | String with the maximum current.
18 |  | StrAMin |  |  | int16 |  | A_SF | A |  |  |  | Min String Current | Minimum current of any string in the bank. | Measurement.
19 |  | StrAMinStr |  |  | uint16 | [6 empty] | Min String Current String | String with the minimum current.
20 |  | StrAAvg |  |  | int16 |  | A_SF | A |  |  |  | Average String Current | Average string current for all strings in the bank. | Calculation based on measurements.
21 |  | NCellBal |  |  | uint16 | [6 empty] | Battery Cell Balancing Count | Total number of cells that are currently being balanced.
22 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
23 |  | ModTmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperatures.
24 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string currents.
25 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for string state of health.
26 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string state of charge.
27 |  | V_SF |  |  | sunssf | [7 empty] | Scale factor for string voltage.
|  | lithium_ion_bank.string |  | NStr | group
| 0 | StrNMod |  |  | uint16 |  |  |  |  | M |  | Module Count | Count of modules in the string.
| 1 | StrSt |  |  | bitfield32 |  |  |  |  | M |  | String Status | Current status of the string.
|  | STRING_ENABLED | 0
|  | CONTACTOR_STATUS | 1
| 3 | StrConFail |  |  | enum16 | [6 empty] | Connection Failure Reason
|  | NO_FAILURE | 0
|  | BUTTON_PUSHED | 1
|  | STR_GROUND_FAULT | 2
|  | OUTSIDE_VOLTAGE_RANGE | 3
|  | STRING_NOT_ENABLED | 4
|  | FUSE_OPEN | 5
|  | CONTACTOR_FAILURE | 6
|  | PRECHARGE_FAILURE | 7
|  | STRING_FAULT | 8
| 4 | StrSoC |  |  | uint16 |  | SoC_SF | % |  | M |  | String State of Charge | Battery string state of charge, expressed as a percentage.
| 5 | StrSoH |  |  | uint16 |  | SoH_SF | % |  |  |  | String State of Health | Battery string state of health, expressed as a percentage.
| 6 | StrA |  |  | int16 |  | A_SF | A |  | M |  | String Current | String current measurement.
| 7 | StrCellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the string.
| 8 | StrCellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the maximum cell voltage.
| 9 | StrCellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the string.
| 10 | StrCellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the minimum cell voltage.
| 11 | StrCellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the string.
| 12 | StrModTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Module Temperature | Maximum temperature for all modules in the bank.
| 13 | StrModTmpMaxMod |  |  | uint16 | [6 empty] | Max Module Temperature Module | Module with the maximum temperature.
| 14 | StrModTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Module Temperature | Minimum temperature for all modules in the bank.
| 15 | StrModTmpMinMod |  |  | uint16 | [6 empty] | Min Module Temperature Module | Module with the minimum temperature.
| 16 | StrModTmpAvg |  |  | int16 |  | ModTmp_SF | C |  | M |  | Average Module Temperature | Average temperature for all modules in the bank.
| 17 | StrDisRsn |  |  | enum16 | [6 empty] | Disabled Reason | Reason why the string is currently disabled.
|  | NONE | 0
|  | FAULT | 1
|  | MAINTENANCE | 2
|  | EXTERNAL | 3
|  | OTHER | 4
| 18 | StrConSt |  |  | bitfield32 | [6 empty] | Contactor Status | Status of the contactor(s) for the string.
|  | CONTACTOR_0 | 0
|  | CONTACTOR_1 | 1
|  | CONTACTOR_2 | 2
|  | CONTACTOR_3 | 3
|  | CONTACTOR_4 | 4
|  | CONTACTOR_5 | 5
|  | CONTACTOR_6 | 6
|  | CONTACTOR_7 | 7
|  | CONTACTOR_8 | 8
|  | CONTACTOR_9 | 9
|  | CONTACTOR_10 | 10
|  | CONTACTOR_11 | 11
|  | CONTACTOR_12 | 12
|  | CONTACTOR_13 | 13
|  | CONTACTOR_14 | 14
|  | CONTACTOR_15 | 15
|  | CONTACTOR_16 | 16
|  | CONTACTOR_17 | 17
|  | CONTACTOR_18 | 18
|  | CONTACTOR_19 | 19
|  | CONTACTOR_20 | 20
|  | CONTACTOR_21 | 21
|  | CONTACTOR_22 | 22
|  | CONTACTOR_23 | 23
|  | CONTACTOR_24 | 24
|  | CONTACTOR_25 | 25
|  | CONTACTOR_26 | 26
|  | CONTACTOR_27 | 27
|  | CONTACTOR_28 | 28
|  | CONTACTOR_29 | 29
|  | CONTACTOR_30 | 30
| 20 | StrEvt1 |  |  | bitfield32 |  |  |  |  | M |  | String Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_1 | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_2 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
| 22 | StrEvt2 |  |  | bitfield32 | [6 empty] | String Event 2 | Alarms, warnings and status values. Bit flags.
| 24 | StrEvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor String Event Bitfield 1 | Vendor defined events.
| 26 | StrEvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor String Event Bitfield 2 | Vendor defined events.
| 28 | StrSetEna |  |  | enum16 |  |  |  | RW |  |  | Enable/Disable String | Enables and disables the string.
|  | ENABLE_STRING | 1
|  | DISABLE_STRING | 2
| 29 | StrSetCon |  |  | enum16 |  |  |  | RW |  |  | Connect/Disconnect String | Connects and disconnects the string.
|  | CONNECT_STRING | 1
|  | DISCONNECT_STRING | 2
| 30 | Pad1 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
| 31 | Pad2 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.

## 804
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lithium_ion_string |  |  | group | [6 empty] | Lithium-Ion String Model
0 |  | ID | 804 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Idx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string within the bank. | Indices are one-based.
3 |  | NMod |  |  | uint16 |  |  |  |  | M |  | Module Count | Count of modules in the string.
4 |  | St |  |  | bitfield32 |  |  |  |  | M |  | String Status | Current status of the string.
|  | STRING_ENABLED | 0
|  | CONTACTOR_STATUS | 1
6 |  | ConFail |  |  | enum16 | [6 empty] | Connection Failure Reason
|  | NO_FAILURE | 0
|  | BUTTON_PUSHED | 1
|  | STR_GROUND_FAULT | 2
|  | OUTSIDE_VOLTAGE_RANGE | 3
|  | STRING_NOT_ENABLED | 4
|  | FUSE_OPEN | 5
|  | CONTACTOR_FAILURE | 6
|  | PRECHARGE_FAILURE | 7
|  | STRING_FAULT | 8
7 |  | NCellBal |  |  | uint16 | [6 empty] | String Cell Balancing Count | Number of cells currently being balanced in the string.
8 |  | SoC |  |  | uint16 |  | SoC_SF | % |  | M |  | String State of Charge | Battery string state of charge, expressed as a percentage. | Measurement.
9 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | String Depth of Discharge | Depth of discharge for the string, expressed as a percentage. | Measurement.
10 |  | NCyc |  |  | uint32 | [6 empty] | String Cycle Count | Number of discharge cycles executed upon the string.
12 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | String State of Health | Battery string state of health, expressed as a percentage. | Measurement.
13 |  | A |  |  | int16 |  | A_SF | A |  | M |  | String Current | String current measurement. | Measurement.
14 |  | V |  |  | uint16 |  | V_SF | V |  |  |  | String Voltage | String voltage measurement. | Measurement.
15 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the string. | Measurement.
16 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with maximum cell voltage.
17 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the string. | Measurement.
18 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with minimum cell voltage.
19 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the string. | Calculation based on measurements.
20 |  | ModTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Module Temperature | Maximum temperature for all modules in the string. | Measurement.
21 |  | ModTmpMaxMod |  |  | uint16 |  |  |  |  | M |  | Max Module Temperature Module | Module with the maximum temperature.
22 |  | ModTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Module Temperature | Minimum temperature for all modules in the string. | Measurement.
23 |  | ModTmpMinMod |  |  | uint16 |  |  |  |  | M |  | Min Module Temperature Module | Module with the minimum temperature.
24 |  | ModTmpAvg |  |  | int16 |  | ModTmp_SF | C |  | M |  | Average Module Temperature | Average temperature for all modules in the string. | Calculation based on measurements.
25 |  | Pad1 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
26 |  | ConSt |  |  | bitfield32 | [6 empty] | Contactor Status | Status of the contactor(s) for the string.
|  | CONTACTOR_0 | 0
|  | CONTACTOR_1 | 1
|  | CONTACTOR_2 | 2
|  | CONTACTOR_3 | 3
|  | CONTACTOR_4 | 4
|  | CONTACTOR_5 | 5
|  | CONTACTOR_6 | 6
|  | CONTACTOR_7 | 7
|  | CONTACTOR_8 | 8
|  | CONTACTOR_9 | 9
|  | CONTACTOR_10 | 10
|  | CONTACTOR_11 | 11
|  | CONTACTOR_12 | 12
|  | CONTACTOR_13 | 13
|  | CONTACTOR_14 | 14
|  | CONTACTOR_15 | 15
|  | CONTACTOR_16 | 16
|  | CONTACTOR_17 | 17
|  | CONTACTOR_18 | 18
|  | CONTACTOR_19 | 19
|  | CONTACTOR_20 | 20
|  | CONTACTOR_21 | 21
|  | CONTACTOR_22 | 22
|  | CONTACTOR_23 | 23
|  | CONTACTOR_24 | 24
|  | CONTACTOR_25 | 25
|  | CONTACTOR_26 | 26
|  | CONTACTOR_27 | 27
|  | CONTACTOR_28 | 28
|  | CONTACTOR_29 | 29
|  | CONTACTOR_30 | 30
28 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | String Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_1 | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_2 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
30 |  | Evt2 |  |  | bitfield32 | [6 empty] | String Event 2 | Alarms, warnings and status values. Bit flags. | Reserved for future use.
32 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events.
34 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events.
36 |  | SetEna |  |  | enum16 |  |  |  | RW |  |  | Enable/Disable String | Enables and disables the string. Should reset to 0 upon completion.
37 |  | SetCon |  |  | enum16 |  |  |  | RW |  |  | Connect/Disconnect String | Connects and disconnects the string. | Should reset to 0 upon completion.
|  | CONNECT_STRING | 1
|  | DISCONNECT_STRING | 2
38 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string state of charge.
39 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for string state of health.
40 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for string depth of discharge.
41 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string current.
42 |  | V_SF |  |  | sunssf | [7 empty] | Scale factor for string voltage.
43 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
44 |  | ModTmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperature.
45 |  | Pad2 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
46 |  | Pad3 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
47 |  | Pad4 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
|  | lithium_ion_string.lithium_ion_string_module |  | NMod | group
| 0 | ModNCell |  |  | uint16 |  |  |  |  | M |  | Module Cell Count | Count of all cells in the module.
| 1 | ModSoC |  |  | uint16 |  | SoC_SF | % |  |  |  | Module SoC | Module state of charge, expressed as a percentage.
| 2 | ModSoH |  |  | uint16 |  | SoH_SF | % |  |  |  | Module SoH | Module state of health, expressed as a percentage.
| 3 | ModCellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the module.
| 4 | ModCellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with maximum voltage.
| 5 | ModCellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the module.
| 6 | ModCellVMinCell |  |  | uint16 | [6 empty] | Min Cell Voltage Cell | Cell with minimum voltage.
| 7 | ModCellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the module.
| 8 | ModCellTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Cell Temperature | Maximum temperature for all cells in the module.
| 9 | ModCellTmpMaxCell |  |  | uint16 | [6 empty] | Max Cell Temperature Cell | Cell with maximum temperature.
| 10 | ModCellTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Cell Temperature | Minimum temperature for all cells in the module.
| 11 | ModCellTmpMinCell |  |  | uint16 | [6 empty] | Min Cell Temperature Cell | Cell with minimum temperature.
| 12 | ModCellTmpAvg |  |  | int16 |  | ModTmp_SF | C |  | M |  | Average Cell Temperature | Average temperature for all cells in the module.
| 13 | Pad5 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
| 14 | Pad6 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
| 15 | Pad7 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.

## 805
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lithium-ion-module |  |  | group | [6 empty] | Lithium-Ion Module Model
0 |  | ID | 805 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | StrIdx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string containing the module. | Indices are one-based.
3 |  | ModIdx |  |  | uint16 |  |  |  |  | M |  | Module Index | Index of the module within the string. | Indices are one-based.
4 |  | NCell |  |  | uint16 |  |  |  |  | M |  | Module Cell Count | Count of all cells in the module.
5 |  | SoC |  |  | uint16 |  | SoC_SF | % |  |  |  | Module SoC | Module state of charge, expressed as a percentage.
6 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | Depth of Discharge | Depth of discharge for the module. | Measurement.
7 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | Module SoH | Module state of health, expressed as a percentage.
8 |  | NCyc |  |  | uint32 | [6 empty] | Cycle Count | Count of cycles executed.
10 |  | V |  |  | uint16 |  | V_SF | V |  | M |  | Module Voltage | Voltage of the module. | Measurement.
11 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the module. | Measurement.
12 |  | CellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with the maximum voltage.
13 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the module. | Measurement.
14 |  | CellVMinCell |  |  | uint16 | [6 empty] | Min Cell Voltage Cell | Cell with the minimum voltage.
15 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the module. | Calculation based on measurements.
16 |  | CellTmpMax |  |  | int16 |  | Tmp_SF | C |  | M |  | Max Cell Temperature | Maximum temperature for all cells in the module. | Measurement.
17 |  | CellTmpMaxCell |  |  | uint16 | [6 empty] | Max Cell Temperature Cell | Cell with the maximum cell temperature.
18 |  | CellTmpMin |  |  | int16 |  | Tmp_SF | C |  | M |  | Min Cell Temperature | Minimum temperature for all cells in the module. | Measurement.
19 |  | CellTmpMinCell |  |  | uint16 | [6 empty] | Min Cell Temperature Cell | Cell with the minimum cell temperature.
20 |  | CellTmpAvg |  |  | int16 |  | Tmp_SF | C |  | M |  | Average Cell Temperature | Average temperature for all cells in the module. | Calculation based on measurements.
21 |  | NCellBal |  |  | uint16 | [6 empty] | Balanced Cell Count | Number of cells currently being balanced in the module.
22 |  | SN |  |  | string | 16 | [5 empty] | Serial Number | Serial number for the module.
38 |  | SoC_SF |  |  | sunssf | [7 empty] | Scale factor for module state of charge.
39 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for module state of health.
40 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for module depth of discharge.
41 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module voltage.
42 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
43 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperature.
|  | lithium-ion-module.lithium-ion-module-cell |  | 0 | group
| 0 | CellV |  |  | uint16 |  | CellV_SF | V |  | M |  | Cell Voltage | Cell terminal voltage.
| 1 | CellTmp |  |  | int16 |  | Tmp_SF | C |  | M |  | Cell Temperature | Cell temperature.
| 2 | CellSt |  |  | bitfield32 | [6 empty] | Cell Status | Status of the cell.
|  | CELL_IS_BALANCING | 0

## 806
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | flow_battery |  |  | group | [6 empty] | Flow Battery Model
0 |  | ID | 806 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | BatTBD |  |  | uint16 |  |  |  |  | M |  | Battery Points To Be Determined
|  | flow_battery.battery_string |  | 0 | group
| 0 | BatStTBD |  |  | uint16 |  |  |  |  | M |  | Battery String Points To Be Determined

## 807
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | flow_battery_string |  |  | group | [6 empty] | Flow Battery String Model
0 |  | ID | 807 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Idx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string within the bank. | Indices are one-based.
3 |  | NMod |  |  | uint16 |  |  |  |  | M |  | Module Count | Number of modules in this string.
4 |  | NModCon |  |  | uint16 |  |  |  |  | M |  | Connected Module Count | Number of electrically connected modules in this string.
5 |  | ModVMax |  |  | uint16 |  | ModV_SF | V |  | M |  | Max Module Voltage | Maximum voltage for all modules in the string. | Measurement.
6 |  | ModVMaxMod |  |  | uint16 | [6 empty] | Max Module Voltage Module | Module with the maximum voltage.
7 |  | ModVMin |  |  | uint16 |  | ModV_SF | V |  | M |  | Min Module Voltage | Minimum voltage for all modules in the string. | Measurement.
8 |  | ModVMinMod |  |  | uint16 | [6 empty] | Min Module Voltage Module | Module with the minimum voltage.
9 |  | ModVAvg |  |  | uint16 |  | ModV_SF | V |  | M |  | Average Module Voltage | Average voltage for all modules in the string. | Calculation based on measurements.
10 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Max Cell Voltage | Maximum voltage for all cells in the string. | Measurement.
11 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with the maximum voltage.
12 |  | CellVMaxStk |  |  | uint16 | [6 empty] | Max Cell Voltage Stack | Stack containing the cell with the maximum voltage.
13 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Min Cell Voltage | Minimum voltage for all cells in the string. | Measurement.
14 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with the minimum voltage.
15 |  | CellVMinStk |  |  | uint16 | [6 empty] | Min Cell Voltage Stack | Stack containing the cell with the minimum voltage.
16 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average voltage for all cells in the string. | Calculation based on measurements.
17 |  | TmpMax |  |  | int16 |  | Tmp_SF | C |  | M |  | Max Temperature | Maximum electrolyte temperature for all modules in the string. | Measurement.
18 |  | TmpMaxMod |  |  | uint16 | [6 empty] | Max Temperature Module | Module with the maximum temperature.
19 |  | TmpMin |  |  | int16 |  | Tmp_SF | C |  | M |  | Min Temperature | Minimum electrolyte temperature for all modules in the string. | Measurement.
20 |  | TmpMinMod |  |  | uint16 | [6 empty] | Min Temperature Module | Module with the minimum temperature.
21 |  | TmpAvg |  |  | int16 |  | Tmp_SF | C |  | M |  | Average Temperature | Average electrolyte temperature for all modules in the string. | Calculation based on measurements.
22 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | String Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | RESERVED_1 | 18
|  | RESERVED_2 | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_3 | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | FIRE_ALARM | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
24 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | String Event 2 | Alarms, warnings and status values. Bit flags.
|  | LEAK_ALARM | 0
|  | PUMP_ALARM | 1
|  | HIGH_PRESSURE_ALARM | 2
|  | HIGH_PRESSURE_WARNING | 3
|  | LOW_FLOW_ALARM | 4
|  | LOW_FLOW_WARNING | 5
26 |  | EvtVnd1 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 1 | Vendor defined events.
28 |  | EvtVnd2 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 2 | Vendor defined events.
30 |  | ModV_SF |  |  | sunssf |  |  |  |  | M
31 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for voltage.
32 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for temperature.
33 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for state of charge.
34 |  | OCV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for open circuit voltage.
35 |  | Pad1 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
|  | flow_battery_string.module |  | 0 | group
| 0 | ModIdx |  |  | uint16 |  |  |  |  | M |  | Module Index | Index of the module within the string.
| 1 | ModNStk |  |  | uint16 |  |  |  |  | M |  | Stack Count | Number of stacks in this module.
| 2 | ModSt |  |  | bitfield32 |  |  |  |  | M |  | Module Status | Current status of the module.
|  | MODULE_ENABLED | 0
|  | CONTACTOR_STATUS | 1
| 4 | ModSoC |  |  | uint16 |  | SoC_SF | % |  | M |  | Module State of Charge | State of charge for this module.
| 5 | ModOCV |  |  | uint16 |  | OCV_SF | V |  | M |  | Open Circuit Voltage | Open circuit voltage for this module.
| 6 | ModV |  |  | uint16 |  | ModV_SF | V |  | M |  | External Voltage | External voltage fo this module.
| 7 | ModCellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Maximum Cell Voltage | Maximum voltage for all cells in this module.
| 8 | ModCellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with the maximum cell voltage.
| 9 | ModCellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Minimum Cell Voltage | Minimum voltage for all cells in this module.
| 10 | ModCellVMinCell |  |  | uint16 | [6 empty] | Min Cell Voltage Cell | Cell with the minimum cell voltage.
| 11 | ModCellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average voltage for all cells in this module.
| 12 | ModAnoTmp |  |  | uint16 |  | Tmp_SF | C |  |  |  | Anolyte Temperature
| 13 | ModCatTmp |  |  | uint16 |  | Tmp_SF | C |  |  |  | Catholyte Temperature
| 14 | ModConSt |  |  | bitfield32 | [6 empty] | Contactor Status
|  | CONTACTOR_0 | 0
|  | CONTACTOR_1 | 1
|  | CONTACTOR_2 | 2
|  | CONTACTOR_3 | 3
|  | CONTACTOR_4 | 4
|  | CONTACTOR_5 | 5
|  | CONTACTOR_6 | 6
|  | CONTACTOR_7 | 7
|  | CONTACTOR_8 | 8
|  | CONTACTOR_9 | 9
|  | CONTACTOR_10 | 10
|  | CONTACTOR_11 | 11
|  | CONTACTOR_12 | 12
|  | CONTACTOR_13 | 13
|  | CONTACTOR_14 | 14
|  | CONTACTOR_15 | 15
|  | CONTACTOR_16 | 16
|  | CONTACTOR_17 | 17
|  | CONTACTOR_18 | 18
|  | CONTACTOR_19 | 19
|  | CONTACTOR_20 | 20
|  | CONTACTOR_21 | 21
|  | CONTACTOR_22 | 22
|  | CONTACTOR_23 | 23
|  | CONTACTOR_24 | 24
|  | CONTACTOR_25 | 25
|  | CONTACTOR_26 | 26
|  | CONTACTOR_27 | 27
|  | CONTACTOR_28 | 28
|  | CONTACTOR_29 | 29
|  | CONTACTOR_30 | 30
| 16 | ModEvt1 |  |  | bitfield32 |  |  |  |  | M |  | Module Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | RESERVED_1 | 18
|  | RESERVED_2 | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_3 | 24
|  | RESERVED_4 | 25
|  | RESERVED_5 | 26
|  | FIRE_ALARM | 27
|  | MODULE_CONFIGURATION_ALARM | 28
|  | MODULE_CONFIGURATION_WARNING | 29
| 18 | ModEvt2 |  |  | bitfield32 |  |  |  |  | M |  | Module Event 2 | Alarms, warnings and status values. Bit flags.
|  | LEAK_ALARM | 0
|  | PUMP_ALARM | 1
|  | HIGH_PRESSURE_ALARM | 2
|  | HIGH_PRESSURE_WARNING | 3
|  | LOW_FLOW_ALARM | 4
|  | LOW_FLOW_WARNING | 5
| 20 | ModConFail |  |  | enum16 | [6 empty] | Connection Failure Reason
|  | NO_FAILURE | 0
|  | BUTTON_PUSHED | 1
|  | MODULE_GROUND_FAULT | 2
|  | OUTSIDE_VOLTAGE_RANGE | 3
|  | MODULE_NOT_ENABLED | 4
|  | FUSE_OPEN | 5
|  | CONTACTOR_FAILURE | 6
|  | PRECHARGE_FAILURE | 7
|  | MODULE_FAULT | 8
| 21 | ModSetEna |  |  | enum16 |  |  |  | RW |  |  | Enable/Disable Module | Enables and disables the module.
|  | ENABLE_MODULE | 1
|  | DISABLE_MODULE | 2
| 22 | ModSetCon |  |  | enum16 |  |  |  | RW |  |  | Connect/Disconnect Module | Connects and disconnects the module.
|  | CONNECT_MODULE | 1
|  | DISCONNECT_MODULE | 2
| 23 | ModDisRsn |  |  | enum16 | [6 empty] | Disabled Reason | Reason why the module is currently disabled.
|  | NONE | 0
|  | FAULT | 1
|  | MAINTENANCE | 2
|  | EXTERNAL | 3
|  | OTHER | 4

## 808
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | flow_battery_module |  |  | group | [6 empty] | Flow Battery Module Model
0 |  | ID | 808 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ModuleTBD |  |  | uint16 |  |  |  |  | M |  | Module Points To Be Determined
|  | flow_battery_module.stack |  | 0 | group
| 0 | StackTBD |  |  | uint16 |  |  |  |  | M |  | Stack Points To Be Determined

## 809
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | flow_battery_stack |  |  | group | [6 empty] | Flow Battery Stack Model
0 |  | ID | 809 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | StackTBD |  |  | uint16 |  |  |  |  | M |  | Stack Points To Be Determined
|  | flow_battery_stack.cell |  | 0 | group
| 0 | CellTBD |  |  | uint16 |  |  |  |  | M |  | Cell Points To Be Determined

## 63001
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_63001 |  |  | group | [6 empty] | SunSpec Test Model 1
0 |  | ID | 63001 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | sunssf_1 |  |  | sunssf
3 |  | sunssf_2 |  |  | sunssf
4 |  | sunssf_3 |  |  | sunssf
5 |  | sunssf_4 |  |  | sunssf
6 |  | int16_1 |  |  | int16 |  | sunssf_1
7 |  | int16_2 |  |  | int16 |  | sunssf_2
8 |  | int16_3 |  |  | int16 |  | sunssf_3
9 |  | int16_4 |  |  | int16 |  | sunssf_4 |  | RW
10 |  | int16_5 |  |  | int16
11 |  | int16_u |  |  | int16
12 |  | uint16_1 |  |  | uint16 |  | sunssf_1
13 |  | uint16_2 |  |  | uint16 |  | sunssf_2
14 |  | uint16_3 |  |  | uint16 |  | sunssf_3
15 |  | uint16_4 |  |  | uint16 |  | sunssf_4 |  | RW
16 |  | uint16_5 |  |  | uint16
17 |  | uint16_u |  |  | uint16
18 |  | acc16 |  |  | acc16
19 |  | acc16_u |  |  | acc16
20 |  | enum16 |  |  | enum16
21 |  | enum16_u |  |  | enum16
22 |  | bitfield16 |  |  | bitfield16
23 |  | bitfield16_u |  |  | bitfield16
24 |  | int32_1 |  |  | int32 |  | sunssf_5
26 |  | int32_2 |  |  | int32 |  | sunssf_6
28 |  | int32_3 |  |  | int32 |  | sunssf_7 |  | RW
30 |  | int32_4 |  |  | int32
32 |  | int32_5 |  |  | int32
34 |  | int32_u |  |  | int32
36 |  | uint32_1 |  |  | uint32 |  | sunssf_5
38 |  | uint32_2 |  |  | uint32 |  | sunssf_6
40 |  | uint32_3 |  |  | uint32 |  | sunssf_7 |  | RW
42 |  | uint32_4 |  |  | uint32 |  | 1
44 |  | uint32_5 |  |  | uint32
46 |  | uint32_u |  |  | uint32
48 |  | acc32 |  |  | acc32
50 |  | acc32_u |  |  | acc32
52 |  | enum32 |  |  | enum32
54 |  | enum32_u |  |  | enum32
56 |  | bitfield32 |  |  | bitfield32
58 |  | bitfield32_u |  |  | bitfield32
60 |  | ipaddr |  |  | ipaddr |  |  |  | RW
62 |  | ipaddr_u |  |  | ipaddr
64 |  | int64 |  |  | int64 |  |  |  | RW
68 |  | int64_u |  |  | int64
72 |  | acc64 |  |  | acc64
76 |  | acc64_u |  |  | acc64
80 |  | ipv6addr |  |  | ipv6addr
88 |  | ipv6addr_u |  |  | ipv6addr
96 |  | float32 |  |  | float32 |  |  |  | RW
98 |  | float32_u |  |  | float32
100 |  | string |  |  | string | 16 |  |  | RW
116 |  | string_u |  |  | string | 16
132 |  | sunssf_5 |  |  | sunssf
133 |  | sunssf_6 |  |  | sunssf
134 |  | sunssf_7 |  |  | sunssf
135 |  | pad_1 |  |  | pad
|  | model_63001.repeating |  | 0 | group
| 0 | sunssf_8 |  |  | sunssf
| 1 | int16_11 |  |  | int16 |  | sunssf_8 |  | RW
| 2 | int16_12 |  |  | int16 |  | sunssf_9
| 3 | int16_u |  |  | int16
| 4 | uint16_11 |  |  | uint16 |  | sunssf_8 |  | RW
| 5 | uint16_12 |  |  | uint16 |  | sunssf_9
| 6 | uint16_13 |  |  | uint16
| 7 | uint16_u |  |  | uint16
| 8 | int32 |  |  | int32 |  | sunssf_1 |  | RW
| 10 | int32_u |  |  | int32
| 12 | uint32 |  |  | uint32 |  | sunssf_9 |  | RW
| 14 | uint32_u |  |  | uint32
| 16 | sunssf_9 |  |  | sunssf
| 17 | pad_2 |  |  | pad

## 63002
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_63002 |  |  | group | [6 empty] | SunSpec Test Model 2
0 |  | ID | 63002 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | model_63002.repeating |  | 0 | group
| 0 | sunssf_1 |  |  | sunssf
| 1 | int16_1 |  |  | int16 |  | sunssf_1 |  | RW
| 2 | int16_2 |  |  | int16 |  | sunssf_2
| 3 | sunssf_2 |  |  | sunssf

## 64001
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_64001 |  |  | group | [6 empty] | Veris Status and Configuration
0 |  | ID | 64001 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Cmd |  |  | enum16 |  |  |  | RW |  |  | Command Code
3 |  | HWRev |  |  | uint16 | [6 empty] | Hardware Revision
4 |  | RSFWRev |  |  | uint16 | [6 empty] | RS FW Revision
5 |  | OSFWRev |  |  | uint16 | [6 empty] | OS FW Revision
6 |  | ProdRev |  |  | string | 2 | [5 empty] | Product Revision
8 |  | Boots |  |  | uint16 | [6 empty] | Boot Count
9 |  | Switch |  |  | bitfield16 | [6 empty] | DIP Switches
10 |  | Sensors |  |  | uint16 | [6 empty] | Num Detected Sensors
11 |  | Talking |  |  | uint16 | [6 empty] | Num Communicating Sensors
12 |  | Status |  |  | bitfield16 | [6 empty] | System Status
13 |  | Config |  |  | bitfield16 | [6 empty] | System Configuration
14 |  | LEDblink |  |  | uint16 |  |  | Pct |  |  |  | LED Blink Threshold
15 |  | LEDon |  |  | uint16 |  |  | Pct |  |  |  | LED On Threshold
16 |  | Reserved |  |  | uint16
17 |  | Loc |  |  | string | 16 | [5 empty] | Location String
33 |  | S1ID |  |  | enum16 | [6 empty] | Sensor 1 Unit ID
34 |  | S1Addr |  |  | uint16 | [6 empty] | Sensor 1 Address
35 |  | S1OSVer |  |  | uint16 | [6 empty] | Sensor 1 OS Version
36 |  | S1Ver |  |  | string | 2 | [5 empty] | Sensor 1 Product Version
38 |  | S1Serial |  |  | string | 5 | [5 empty] | Sensor 1 Serial Num
43 |  | S2ID |  |  | enum16 | [6 empty] | Sensor 2 Unit ID
44 |  | S2Addr |  |  | uint16 | [6 empty] | Sensor 2 Address
45 |  | S2OSVer |  |  | uint16 | [6 empty] | Sensor 2 OS Version
46 |  | S2Ver |  |  | string | 2 | [5 empty] | Sensor 2 Product Version
48 |  | S2Serial |  |  | string | 5 | [5 empty] | Sensor 2 Serial Num
53 |  | S3ID |  |  | enum16 | [6 empty] | Sensor 3 Unit ID
54 |  | S3Addr |  |  | uint16 | [6 empty] | Sensor 3 Address
55 |  | S3OSVer |  |  | uint16 | [6 empty] | Sensor 3 OS Version
56 |  | S3Ver |  |  | string | 2 | [5 empty] | Sensor 3 Product Version
58 |  | S3Serial |  |  | string | 5 | [5 empty] | Sensor 3 Serial Num
63 |  | S4ID |  |  | enum16 | [6 empty] | Sensor 4 Unit ID
64 |  | S4Addr |  |  | uint16 | [6 empty] | Sensor 4 Address
65 |  | S4OSVer |  |  | uint16 | [6 empty] | Sensor 4 OS Version
66 |  | S4Ver |  |  | string | 2 | [5 empty] | Sensor 4 Product Version
68 |  | S4Serial |  |  | string | 5 | [5 empty] | Sensor 4 Serial Num

## 64020
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_64020 |  |  | group | [6 empty] | Mersen GreenString
0 |  | ID | 64020 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Aux0Tmp |  |  | int16 |  |  | C |  |  |  | Aux 0 temperature
3 |  | Aux1Tmp |  |  | int16 |  |  | C |  |  |  | Aux 1 temperature
4 |  | Aux2Tmp |  |  | int16 |  |  | C |  |  |  | Aux 2 temperature
5 |  | Aux3Tmp |  |  | int16 |  |  | C |  |  |  | Aux 3 temperature
6 |  | Aux4Tmp |  |  | int16 |  |  | C |  |  |  | Aux 4 temperature
7 |  | ProbeTmp |  |  | int16 |  |  | C |  | M |  | Probe Temperature
8 |  | MainTmp |  |  | int16 |  |  | C |  | M |  | Main Temperature
9 |  | SensorV_SF |  |  | sunssf |  |  |  |  | M |  | Voltage scale factor for the sensors
10 |  | SensorA_SF |  |  | sunssf |  |  |  |  | M |  | Current scale factor for the sensors
11 |  | SensorHz_SF |  |  | sunssf |  |  |  |  | M |  | Frequency scale factor for the sensors
12 |  | Sensor1Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor1 Voltage | scale of 0-10V
13 |  | Sensor2Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor2 Voltage | scale of 0-10V
14 |  | Sensor3Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor3 Voltage | scale of 0-10V
15 |  | Sensor4Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor4 Voltage | scale of 0-10V
16 |  | Sensor5Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor5 Voltage | scale of 0-10V
17 |  | Sensor6Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor6 Voltage | scale of 0-10V
18 |  | Sensor7Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor7 Voltage | scale of 0-10V
19 |  | Sensor1Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor1 Current | scale of 4-20mA
20 |  | Sensor2Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor2 Current | in 4-20mA or 4-20mA
21 |  | Sensor3Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor3 Current | in 4-20mA or 4-20mA
22 |  | Sensor4Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor4 Current | in 4-20mA or 4-20mA
23 |  | Sensor5Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor5 Current | in 4-20mA or 4-20mA
24 |  | Sensor6Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor6 Current | in 4-20mA or 4-20mA
25 |  | Sensor7Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor7 Current | in 4-20mA or 4-20mA
26 |  | Sensor8 |  |  | uint16 |  | SensorHz_SF | Hz |  |  |  | Sensor8 frequency | frequency in Hz
27 |  | Relay1 |  |  | uint16 | [6 empty] | Relay 1 state
28 |  | Relay2 |  |  | uint16 | [6 empty] | Relay 2 state
29 |  | Relay3 |  |  | uint16 | [6 empty] | Relay 3 state
30 |  | ResetAccumulators |  |  | uint16 | [6 empty] | Reset the accumulators | always 0 in reading, used the code 0xC0DA during the writing for resetting them
31 |  | Reset |  |  | uint16 | [6 empty] | Reset the system | always 0 in reading, used the code 0xC0DA during the writing for resetting the system
|  | model_64020.repeating |  | 0 | group
| 0 | SerialNumber |  |  | string | 9 |  |  |  | M |  | Serial number | strings of 16 characters
| 9 | Firmware |  |  | string | 6 |  |  |  | M |  | Firmware version | string of 11 characters
| 15 | Hardware |  |  | uint16 |  |  |  |  | M |  | Hardware version

## 64101
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_64101 |  |  | group | [6 empty] | Eltek Inverter Extension
0 |  | ID | 64101 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Eltek_Country_Code |  |  | uint16
3 |  | Eltek_Feeding_Phase |  |  | uint16
4 |  | Eltek_APD_Method |  |  | uint16
5 |  | Eltek_APD_Power_Ref |  |  | uint16
6 |  | Eltek_RPS_Method |  |  | uint16
7 |  | Eltek_RPS_Q_Ref |  |  | uint16
8 |  | Eltek_RPS_CosPhi_Ref |  |  | int16

## 64111
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_64111 |  |  | group | [6 empty] | Basic Charge Controller
0 |  | ID | 64111 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Port |  |  | uint16 |  |  |  |  | M |  | Port Number
3 |  | V_SF |  |  | sunssf |  |  |  |  | M
4 |  | A_SF |  |  | sunssf |  |  |  |  | M
5 |  | P_SF |  |  | sunssf |  |  |  |  | M
6 |  | AH_SF |  |  | sunssf |  |  |  |  | M
7 |  | KWH_SF |  |  | sunssf |  |  |  |  | M
8 |  | BattV |  |  | uint16 |  | V_SF | V |  | M |  | Battery Voltage
9 |  | ArrayV |  |  | uint16 |  | V_SF | V |  | M |  | Array Voltage
10 |  | OutputA |  |  | uint16 |  | A_SF | A |  | M |  | Output Current
11 |  | InputA |  |  | uint16 |  | P_SF | A |  | M |  | Array Current
12 |  | ChargerSt |  |  | enum16 |  |  |  |  | M |  | Operating State
|  | Off | 0
|  | Float | 1
|  | Bulk | 2
|  | Absorb | 3
|  | EQ | 4
13 |  | OutputW |  |  | uint16 |  | P_SF | W |  | M |  | Output Wattage
14 |  | TodayMinBatV |  |  | uint16 |  | V_SF | V |  | M |  | Today's Minimum Battery Voltage
15 |  | TodayMaxBatV |  |  | uint16 |  | V_SF | V |  | M |  | Today's Maximum Battery Voltage
16 |  | VOCV |  |  | uint16 |  | V_SF | V |  | M |  | VOC
17 |  | TodayMaxVOC |  |  | uint16 |  | V_SF | V |  | M |  | Today's Maximum VOC
18 |  | TodaykWhOutput |  |  | uint16 |  | KWH_SF | kWh |  | M |  | Today's kWh
19 |  | TodayAHOutput |  |  | uint16 |  | AH_SF | AH |  | M |  | Today's AH
20 |  | LifeTimeKWHOut |  |  | uint16 |  | P_SF | kWh |  | M |  | Lifetime kWh
21 |  | LifeTimeAHOut |  |  | uint16 |  | KWH_SF | kAH |  | M |  | Lifetime kAH
22 |  | LifeTimeMaxOut |  |  | uint16 |  | P_SF | W |  | M |  | Lifetime Maximum Output Wattage
23 |  | LifeTimeMaxBatt |  |  | uint16 |  | V_SF | V |  | M |  | Lifetime Maximum Battery Voltage
24 |  | LifeTimeMaxVOC |  |  | uint16 |  | V_SF | V |  | M |  | Lifetime Maximum VOC Voltage

## 64112
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | model_64112 |  |  | group | [6 empty] | OutBack FM Charge Controller
0 |  | ID | 64112 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Port |  |  | uint16 |  |  |  |  | M |  | Port Number
3 |  | V_SF |  |  | sunssf |  |  |  |  | M
4 |  | C_SF |  |  | sunssf |  |  |  |  | M
5 |  | H_SF |  |  | sunssf |  |  |  |  | M
6 |  | P_SF |  |  | sunssf |  |  |  |  | M
7 |  | AH_SF |  |  | sunssf |  |  |  |  | M
8 |  | KWH_SF |  |  | sunssf |  |  |  |  | M
9 |  | CC_Config_fault |  |  | bitfield16 |  |  |  |  | M |  | Faults
10 |  | CC_Config_absorb_V |  |  | uint16 |  | V_SF | V |  | M |  | Absorb
11 |  | CC_Config_absorb_Hr |  |  | uint16 |  | H_SF | Tmh |  | M |  | Absorb Time
12 |  | CC_Config_absorb_End_A |  |  | uint16 |  | V_SF | A |  | M |  | Absorb End
13 |  | CC_Config_rebulk_V |  |  | uint16 |  | V_SF | V |  | M |  | Rebulk
14 |  | CC_Config_float_V |  |  | uint16 |  | V_SF | V |  | M |  | Float
15 |  | CC_Config_max_Chg_A |  |  | uint16 |  | V_SF | A |  | M |  | Maximum Charge
16 |  | CC_Config_equalize_V |  |  | uint16 |  | V_SF | V |  | M |  | Equalize
17 |  | CC_Config_equalize_Hr |  |  | uint16 |  |  | Tmh |  | M |  | Equalize Time
18 |  | CC_Config_auto_equalize |  |  | uint16 |  |  | Tmd |  | M |  | Auto Equalize Interval
19 |  | CC_Config_MPPT_mode |  |  | enum16 |  |  |  |  | M |  | MPPT mode
|  | Auto | 0
|  | U_Pick | 1
|  | Wind | 2
20 |  | CC_Config_sweep_width |  |  | enum16 |  |  |  |  | M |  | Sweep Width
|  | Half | 0
|  | Full | 1
21 |  | CC_Config_sweep_max |  |  | enum16 |  |  |  |  | M |  | Sweep Maximum
|  | Eighty_Percent | 0
|  | Eighty_Five_Percent | 1
|  | Ninty_Percent | 2
|  | Ninty_Nine_Percent | 3
22 |  | CC_Config_U_Pick_Duty_cyc |  |  | uint16 |  | V_SF | Pct |  | M |  | U-Pick PWM Duty Cycle
23 |  | CC_Config_grid_tie |  |  | enum16 |  |  |  |  | M |  | Grid Tie Mode
|  | Disabled | 0
|  | Enabled | 1
24 |  | CC_Config_temp_comp |  |  | enum16 |  |  |  |  | M |  | Temp Comp Mode
|  | Wide | 0
|  | Limited | 1
25 |  | CC_Config_temp_comp_llimt |  |  | uint16 |  | V_SF | V |  | M |  | Temp Comp Lower Limit
26 |  | CC_Config_temp_comp_hlimt |  |  | uint16 |  | V_SF | V |  | M |  | Temp Comp Upper Limit
27 |  | CC_Config_auto_restart |  |  | enum16 |  |  |  |  | M |  | Auto Restart Mode
|  | Off | 0
|  | Every_90_Minutes | 1
|  | Every_90_Minutes_if_Absorb_or_Float | 2
28 |  | CC_Config_wakeup_VOC |  |  | uint16 |  | V_SF | V |  | M |  | Wakeup VOC Change
29 |  | CC_Config_snooze_mode_A |  |  | uint16 |  | V_SF | A |  | M |  | Snooze Mode
30 |  | CC_Config_wakeup_interval |  |  | uint16 |  |  | Tms |  | M |  | Wakeup Interval
31 |  | CC_Config_AUX_mode |  |  | enum16 |  |  |  |  | M |  | AUX Output Mode
|  | Float | 0
|  | Diversion_Relay | 1
|  | Diversion_Solid_St | 2
|  | Low_Batt_Disconnect | 3
|  | Remote | 4
|  | Vent_Fan | 5
|  | PV_Trigger | 6
|  | Error_Output | 7
|  | Night_Light | 8
32 |  | CC_Config_AUX_control |  |  | enum16 |  |  |  |  | M |  | AUX Output Control
|  | Off | 0
|  | Auto | 1
|  | On | 2
33 |  | CC_Config_AUX_state |  |  | enum16 |  |  |  |  | M |  | AUX Output State
|  | Disabled | 0
|  | Enabled | 1
34 |  | CC_Config_AUX_polarity |  |  | enum16 |  |  |  |  | M |  | AUX Output Polarity
|  | Low | 0
|  | High | 1
35 |  | CC_Config_AUX_L_Batt_disc |  |  | uint16 |  | V_SF | V |  | M |  | AUX Low Battery Disconnect
36 |  | CC_Config_AUX_L_Batt_rcon |  |  | uint16 |  | V_SF | V |  | M |  | AUX Low Battery Reconnect
37 |  | CC_Config_AUX_L_Batt_dly |  |  | uint16 |  |  | Tms |  | M |  | AUX Low Battery Disconnect Delay
38 |  | CC_Config_AUX_Vent_fan_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Vent Fan
39 |  | CC_Config_AUX_PV_triggerV |  |  | uint16 |  | V_SF | V |  | M |  | AUX PV Trigger
40 |  | CC_Config_AUX_PV_trg_h_tm |  |  | uint16 |  |  | Tms |  | M |  | AUX PV Trigger Hold Time
41 |  | CC_Config_AUX_Nlite_ThrsV |  |  | uint16 |  | V_SF | V |  | M |  | AUX Night Light Threshold
42 |  | CC_Config_AUX_Nlite_On_tm |  |  | uint16 |  | H_SF | Tmh |  | M |  | AUX Night Light On Time
43 |  | CC_Config_AUX_Nlite_On_hist |  |  | uint16 |  |  | Tms |  | M |  | AUX Night Light On Hysteresis
44 |  | CC_Config_AUX_Nlite_Off_hist |  |  | uint16 |  |  | Tms |  | M |  | AUX Night Light Off Hysteresis
45 |  | CC_Config_AUX_Error_batt_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Error Output Low Battery
46 |  | CC_Config_AUX_Divert_h_time |  |  | uint16 |  | V_SF | Tms |  | M |  | AUX Divert Hold Time
47 |  | CC_Config_AUX_Divert_dly_time |  |  | uint16 |  |  | Tms |  | M |  | AUX Divert Delay Time
48 |  | CC_Config_AUX_Divert_Rel_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Divert Relative
49 |  | CC_Config_AUX_Divert_Hyst_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Divert Hysteresis
50 |  | CC_Config_MajorFWRev |  |  | uint16 |  |  |  |  | M |  | FM CC Major Firmware Number
51 |  | CC_Config_MidFWRev |  |  | uint16 |  |  |  |  | M |  | FM CC Mid Firmware Number
52 |  | CC_Config_MinorFWRev |  |  | uint16 |  |  |  |  | M |  | FM CC Minor Firmware Number
53 |  | CC_Config_DataLog_Day_offset |  |  | uint16 |  |  | Tmd |  | M |  | Set Data Log Day Offset
54 |  | CC_Config_DataLog_Cur_Day_off |  |  | uint16 |  |  | Tmd |  | M |  | Current Data Log Day Offset
55 |  | CC_Config_DataLog_Daily_AH |  |  | uint16 |  |  | Ah |  | M |  | Data Log Daily (Ah)
56 |  | CC_Config_DataLog_Daily_KWH |  |  | uint16 |  | KWH_SF | kWh |  | M |  | Data Log Daily (kWh)
57 |  | CC_Config_DataLog_Max_Out_A |  |  | uint16 |  | V_SF | A |  | M |  | Data Log Daily Maximum Output (A)
58 |  | CC_Config_DataLog_Max_Out_W |  |  | uint16 |  | V_SF | W |  | M |  | Data Log Daily Maximum Output (W)
59 |  | CC_Config_DataLog_Absorb_T |  |  | uint16 |  |  | Tms |  | M |  | Data Log Daily Absorb Time
60 |  | CC_Config_DataLog_Float_T |  |  | uint16 |  |  | Tms |  | M |  | Data Log Daily Float Time
61 |  | CC_Config_DataLog_Min_Batt_V |  |  | uint16 |  | V_SF | V |  | M |  | Data Log Daily Minimum Battery
62 |  | CC_Config_DataLog_Max_Batt_V |  |  | uint16 |  | V_SF | V |  | M |  | Data Log Daily Maximum Battery
63 |  | CC_Config_DataLog_Max_Input_V |  |  | uint16 |  | V_SF | V |  | M |  | Data Log Daily Maximum Input
64 |  | CC_Config_DataLog_Clear |  |  | uint16 |  |  |  |  | M |  | Data Log Clear
65 |  | CC_Config_DataLog_Clr_Comp |  |  | uint16 |  |  |  |  | M |  | Data Log Clear Complement

## 64410
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DCSimInterface |  |  | group | [6 empty] | DC Simulator Control Interface | A generic DC simulator/power supply control interface for DER electrical testing.
0 |  | ID | 64410 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length.
2 |  | VMaxLim |  |  | uint16 |  | V_SF | V | RW |  |  | Maximum Voltage | Upper Voltage Protection Limit
3 |  | PMaxLim |  |  | uint16 |  | W_SF | W | RW |  |  | Maximum Power | Upper Power Protection Limit
4 |  | IMaxLim |  |  | uint16 |  | A_SF | A | RW |  |  | Maximum Current | Upper Current Protection Limit
5 |  | Mode |  |  | enum16 |  |  |  | RW |  |  | CV or CC Mode | Constant Voltage (CV) or Constant Current (CC) Mode
|  | CV | 0 | [8 empty] | CV Mode | Constant Voltage (CV) Mode
|  | CC | 1 | [8 empty] | CC Mode | Constant Current (CC) Mode.
6 |  | Ena |  |  | enum16 |  |  |  | RW |  |  | Power On/Off | Power On/Off
|  | OFF | 0 | [8 empty] | Power Off | Power Off
|  | ON | 1 | [8 empty] | Power On | Power On
7 |  | Reset |  |  | enum16 |  |  |  | RW |  |  | Reset Device | Reset Device
|  | DO_NOT_RESET | 0 | [8 empty] | Do Not Reset Device | Do Not Reset Device
|  | RESET | 1 | [8 empty] | Reset Device | Reset Device
8 |  | VSet |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Setpoint | Voltage Setpoint
9 |  | PSet |  |  | uint16 |  | W_SF | W | RW |  |  | Power Setpoint | Power Setpoint
10 |  | ISet |  |  | uint16 |  | A_SF | A | RW |  |  | Current Setpoint | Current Setpoint
11 |  | EN50530 |  |  | enum16 |  |  |  | RW |  |  | EN50530 Mode | EN50530 Mode - Enable or disable EN50530 profile mode
|  | DO_NOT_EN50530 | 0 | [8 empty] | Do Not Use EN50530 Mode | Do Not Use EN50530 Mode
|  | EN50530 | 1 | [8 empty] | EN50530 Mode | EN50530 Mode
12 |  | Vmpp |  |  | uint16 |  | V_SF | V | RW |  |  | EN50530 MPP Voltage | EN50530 MPP Voltage
13 |  | Pmpp |  |  | uint16 |  | W_SF | W | RW |  |  | EN50530 MPP Power | EN50530 MPP Power
14 |  | GSet |  |  | uint16 |  | G_SF | W/m^2 | RW |  |  | Irradiance Setpoint | Irradiance Setpoint
15 |  | VSlewRate |  |  | uint16 |  | VSlew_SF | V/s | RW |  |  | Voltage Slew Rate | Voltage Slew Rate
16 |  | PSlewRate |  |  | uint16 |  | PSlew_SF | W/s | RW |  |  | Power Slew Rate | Power Slew Rate
17 |  | ISlewRate |  |  | uint16 |  | ISlew_SF | A/s | RW |  |  | Current Slew Rate | Current Slew Rate
18 |  | EnaProf |  |  | enum16 |  |  |  | RW |  |  | Enable Profile | Start/Stop the Profile
|  | STOP | 0 | [8 empty] | Stop Profile | Stop the Profile
|  | START | 1 | [8 empty] | Start Profile | Start the Profile
19 |  | AdptProfReq |  |  | uint16 |  |  |  | RW |  |  | Profile Adoption Request | Index of profile points to adopt. First curve index is 1.
20 |  | AdptProfRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Profile Result | Result of last adopt profile operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Profile update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Profile update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Profile update failed.
21 |  | V |  |  | int32 | [6 empty] | Measured Voltage | Measured Voltage
23 |  | P |  |  | int32 | [6 empty] | Measured Power | Measured Power
25 |  | I |  |  | int32 | [6 empty] | Measured Current | Measured Current
27 |  | Errors |  |  | string | 32 | [5 empty] | Errors | Error States
59 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of profile points supported.
60 |  | NProf |  |  | uint16 |  |  |  |  | M | S | Stored Profile Count | Number of stored profiles supported.
61 |  | W_SF |  |  | sunssf |  |  |  | RW | M | S | Power Scale Factor | Scale factor for power points.
62 |  | V_SF |  |  | sunssf |  |  |  | RW | M | S | Voltage Scale Factor | Scale factor for voltage points.
63 |  | A_SF |  |  | sunssf |  |  |  | RW | M | S | Current Scale Factor | Scale factor for current points.
64 |  | G_SF |  |  | sunssf |  |  |  | RW | M | S | Irradiance Scale Factor | Scale factor for irradiance.
65 |  | Tms_SF |  |  | sunssf |  |  |  | RW | M | S | Time Scale Factor | Scale factor for time points.
66 |  | VSlew_SF |  |  | sunssf |  |  |  | RW | M | S | Voltage Slew Rate Scale Factor | Scale factor for voltage slew rate.
67 |  | PSlew_SF |  |  | sunssf |  |  |  | RW | M | S | Power Slew Rate Scale Factor | Scale factor for power slew rate.
68 |  | ISlew_SF |  |  | sunssf |  |  |  | RW | M | S | Current Slew Rate Scale Factor | Scale factor for current slew rate.
69 |  | Pct_SF |  |  | sunssf |  |  |  | RW | M | S | Percent Scale Factor | Scale factor for percentages.
Stored Pofile Sets - Number of profile sets = NProf - The first set is read-only and indicates the current settings.
|  | DCSimInterface.Prof |  | NProf | group | [6 empty] | Stored Profiles | Stored profile sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points.
| 1 | DeptRef |  |  | bitfield32 |  |  |  | RW | M |  | Dependent References | Profile references.
|  | VOLTAGE | 0 | [8 empty] | Voltage
|  | POWER | 1 | [8 empty] | Power
|  | CURRENT | 2 | [8 empty] | Current
|  | IRRADIANCE | 3 | [8 empty] | Irradiance
Stored Profile Sets - Profile points for each stored profile - Number of profile points contained in NPt
|  | DCSimInterface.Prof.Pt |  | NPt | group | [6 empty] | Stored Profile Points | Stored profile points.
| 0 | Tms |  |  | uint16 |  | Tms_SF | Sec | RW |  |  | Profile Time | Profile time.
| 1 | V |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Point | Profile voltage point in Volts.
| 2 | P |  |  | uint16 |  | W_SF | W | RW |  |  | Power Point | Profile power point in Watts.
| 3 | I |  |  | uint16 |  | A_SF | A | RW |  |  | Current Point | Profile current point in Amps.
| 4 | G |  |  | uint16 |  | Pct_SF | Pct | RW |  |  | Irradiance Point | Profile irradiance point as percentage.

## 64411
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | ACSimInterface |  |  | group | [6 empty] | AC Simulator Control Interface | A generic AC simulator/power supply control interface for DER electrical testing.
0 |  | ID | 64411 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length.
2 |  | Phases |  |  | uint16 |  |  |  | RW |  |  | Active Phases | Set the number of active phases for the power supply
3 |  | PhaseAngle |  |  | uint16 |  |  |  | RW |  |  | Phase Angle | Phase angle (deg) between phases. 0 for signle phase, 120 for two phase, 120 for three phase.
4 |  | VNom |  |  | uint16 |  | V_SF | V | RW |  |  | Nominal Voltage | Nominal L-N Voltage
5 |  | VMax |  |  | uint16 |  | V_SF | V | RW |  |  | Maximum Voltage | Maximum Voltage Protection Level
6 |  | IMax |  |  | uint16 |  | A_SF | A | RW |  |  | Maximum Current | Maximum Current Protection Level
7 |  | Freq |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Frequency | Frequency Setpoint
8 |  | Output |  |  | enum16 |  |  |  | RW |  |  | Output State | AC Output State
|  | OFF | 0 | [8 empty] | Output Off
|  | ON | 1 | [8 empty] | Output On
9 |  | Relay |  |  | enum16 |  |  |  | RW |  |  | Relay State | AC Relay State
|  | OPEN | 0 | [8 empty] | Relay Open
|  | CLOSED | 1 | [8 empty] | Relay Closed
10 |  | Regen |  |  | enum16 |  |  |  | RW |  |  | Regeneration State | Regeneration State
|  | OFF | 0 | [8 empty] | Regen Off
|  | ON | 1 | [8 empty] | Regen On
11 |  | VSet |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Setpoint | Voltage Setpoint (all phases)
12 |  | VSetA |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Setpoint Phase A | Voltage Setpoint Phase A
13 |  | VSetB |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Setpoint Phase B | Voltage Setpoint Phase B
14 |  | VSetC |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Setpoint Phase C | Voltage Setpoint Phase C
15 |  | FreqSlew |  |  | uint16 |  | HzSlew_SF | Hz/s | RW |  |  | Frequency Slew Rate | Frequency Slew Rate
16 |  | VSlew |  |  | uint16 |  | VSlew_SF | V/s | RW |  |  | Voltage Slew Rate | Voltage Slew Rate
17 |  | VA |  |  | int32 |  | V_SF | V |  |  |  | Measured Voltage Phase A | Measured Voltage Phase A
19 |  | VB |  |  | int32 |  | V_SF | V |  |  |  | Measured Voltage Phase B | Measured Voltage Phase B
21 |  | VC |  |  | int32 |  | V_SF | V |  |  |  | Measured Voltage Phase C | Measured Voltage Phase C
23 |  | Hz |  |  | int32 |  | Hz_SF | Hz |  |  |  | Measured Frequency | Measured Frequency
25 |  | IA |  |  | int32 |  | A_SF | A |  |  |  | Measured Current Phase A | Measured Current Phase A
27 |  | IB |  |  | int32 |  | A_SF | A |  |  |  | Measured Current Phase B | Measured Current Phase B
29 |  | IC |  |  | int32 |  | A_SF | A |  |  |  | Measured Current Phase C | Measured Current Phase C
31 |  | VHarA |  |  | string | 150 |  | V |  |  |  | Voltage Harmonics Phase A | Voltage Harmonics Pct, Phase A (comma seperated string for harmonics 1-50)
181 |  | VHarB |  |  | string | 150 |  | V |  |  |  | Voltage Harmonics Phase B | Voltage Harmonics Pct, Phase B (comma seperated string for harmonics 1-50)
331 |  | VHarC |  |  | string | 150 |  | V |  |  |  | Voltage Harmonics Phase C | Voltage Harmonics Pct, Phase C (comma seperated string for harmonics 1-50)
481 |  | IHarA |  |  | string | 150 |  | A |  |  |  | Current Harmonics Phase A | Current Harmonics Pct, Phase A (comma seperated string for harmonics 1-50)
631 |  | IHarB |  |  | string | 150 |  | A |  |  |  | Current Harmonics Phase B | Current Harmonics Pct, Phase B (comma seperated string for harmonics 1-50)
781 |  | IHarC |  |  | string | 150 |  | A |  |  |  | Current Harmonics Phase C | Current Harmonics Pct, Phase C (comma seperated string for harmonics 1-50)
931 |  | IIntHarA |  |  | string | 150 |  | A |  |  |  | Current Interharmonics Phase A | Current Interharmonics Pct, Phase A (comma seperated string for interharmonics 1-50)
1081 |  | IIntHarB |  |  | string | 150 |  | A |  |  |  | Current Interharmonics Phase B | Current Interharmonics Pct, Phase B (comma seperated string for interharmonics 1-50)
1231 |  | IIntHarC |  |  | string | 150 |  | A |  |  |  | Current Interharmonics Phase C | Current Interharmonics Pct, Phase C (comma seperated string for interharmonics 1-50)
1381 |  | VThdA |  |  | uint16 |  | THD_SF | % |  |  |  | Voltage THD Phase A | Voltage THD Phase A
1382 |  | VThdB |  |  | uint16 |  | THD_SF | % |  |  |  | Voltage THD Phase B | Voltage THD Phase B
1383 |  | VThdC |  |  | uint16 |  | THD_SF | % |  |  |  | Voltage THD Phase C | Voltage THD Phase C
1384 |  | IThdA |  |  | uint16 |  | THD_SF | % |  |  |  | Current THD Phase A | Current THD Phase A
1385 |  | IThdB |  |  | uint16 |  | THD_SF | % |  |  |  | Current THD Phase B | Current THD Phase B
1386 |  | IThdC |  |  | uint16 |  | THD_SF | % |  |  |  | Current THD Phase C | Current THD Phase C
1387 |  | EnaProf |  |  | enum16 |  |  |  | RW |  |  | Enable Profile | Start/Stop the AC Profile
|  | STOP | 0 | [8 empty] | Stop Profile
|  | START | 1 | [8 empty] | Start Profile Immediately
|  | TRIGGER | 2 | [8 empty] | Start Profile via External Trigger Signal
1388 |  | ProfRslt |  |  | enum16 |  |  |  |  | M |  | Profile Result | Result of last profile operation.
|  | IN_PROGRESS | 0 | [8 empty] | Profile update in progress.
|  | COMPLETED | 1 | [8 empty] | Profile update completed successfully.
|  | FAILED | 2 | [8 empty] | Profile update failed.
1389 |  | NProf |  |  | uint16 |  |  |  |  | M | S | Stored Profile Count | Number of stored profiles supported.
1390 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Max Profile Point Count | Max profile points in the profiles.
1391 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for voltage points.
1392 |  | A_SF |  |  | sunssf |  |  |  |  | M | S | Current Scale Factor | Scale factor for current points.
1393 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Scale Factor | Scale factor for time points.
1394 |  | Hz_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Scale Factor | Scale factor for frequency points.
1395 |  | HzSlew_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Slew Rate Scale Factor | Scale factor for frequency slew rate.
1396 |  | VSlew_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Slew Rate Scale Factor | Scale factor for voltage slew rate.
1397 |  | THD_SF |  |  | sunssf |  |  |  |  | M | S | THD Scale Factor | Scale factor for THD values.
Stored AC Profile Sets - Number of profile sets = NProf
|  | ACSimInterface.Prof |  | NProf | group | [6 empty] | Stored AC Profiles | Stored AC profile sets.
| 0 | Name |  |  | string | 32 |  |  | RW |  |  | Profile Name | Profile name.
| 32 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points.
Stored AC Profile Sets - Profile points for each stored profile - Number of profile points contained in NPt
|  | ACSimInterface.Prof.Pt |  | NPt | group | [6 empty] | Stored AC Profile Points | Stored AC profile points.
| 0 | Tms |  |  | uint16 |  | Tms_SF | Sec | RW |  |  | Profile Time | Profile time.
| 1 | VA |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Point | Profile voltage phase A point in Volts.
| 2 | VB |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Point Phase B | Profile voltage phase B point in Volts.
| 3 | VC |  |  | uint16 |  | V_SF | V | RW |  |  | Voltage Point Phase C | Profile voltage phase C point in Volts.
| 4 | Hz |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Profile frequency point in Hz.
| 5 | PhaseAngleA |  |  | uint16 |  |  | Degrees | RW |  |  | Phase Angle A | Profile phase A angle in degrees.
| 6 | PhaseAngleB |  |  | uint16 |  |  | Degrees | RW |  |  | Phase Angle B | Profile phase B angle in degrees.
| 7 | PhaseAngleC |  |  | uint16 |  |  | Degrees | RW |  |  | Phase Angle C | Profile phase C angle in degrees.

## 64412
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERExploitation |  |  | group | [6 empty] | DER Cyber Exploitation | Operations that represent a hacked DER device
0 |  | ID | 64412 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length.
2 |  | DAManipulation |  |  | enum16 |  |  |  | RW |  |  | DA Manipulation | Modify the device ID of the DER
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
3 |  | FalsifyDeviceIdentity |  |  | enum16 |  |  |  | RW |  |  | Falsify Device Identity | Change the DER manufacturer and model
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
4 |  | MeasPAlwaysNameplate |  |  | enum16 |  |  |  | RW |  |  | Meas P Always Nameplate | Set the DER meas to always be at nameplate power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
5 |  | MeasQAlwaysMinimum |  |  | enum16 |  |  |  | RW |  |  | Meas Q Always Minimum | Set the DER to always be at minimum reactive power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
6 |  | MeasQAlwaysMaximum |  |  | enum16 |  |  |  | RW |  |  | Meas Q Always Maximum | Set the DER to always be at maximum reactive power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
7 |  | MeasQAlwaysZero |  |  | enum16 |  |  |  | RW |  |  | Meas Q Always Zero | Set the DER to always be at zero reactive power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
8 |  | MeasZeroP |  |  | enum16 |  |  |  | RW |  |  | Meas Zero P | Set the DER to always be at zero P, Q, and S
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
9 |  | MeasInvertQ |  |  | enum16 |  |  |  | RW |  |  | Meas Invert Q | Set the DER to reverse the Q measurement data
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
10 |  | MeasLowV |  |  | enum16 |  |  |  | RW |  |  | Meas Low V | Set the DER to always measure low voltage
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
11 |  | MeasHighV |  |  | enum16 |  |  |  | RW |  |  | Meas High V | Set the DER to always measure high voltage
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
12 |  | MeasLowL1V |  |  | enum16 |  |  |  | RW |  |  | Meas Low L1 V | Set the DER to always measure low line 1 voltage
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
13 |  | MeasHighL1V |  |  | enum16 |  |  |  | RW |  |  | Meas High L1 V | Set the DER to always measure high line 1 voltage
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
14 |  | MeasLowF |  |  | enum16 |  |  |  | RW |  |  | Meas Low F | Set the DER to always measure low frequency
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
15 |  | MeasHighF |  |  | enum16 |  |  |  | RW |  |  | Meas High F | Set the DER to always measure high frequency
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
16 |  | MeasLowAmps |  |  | enum16 |  |  |  | RW |  |  | Meas Low Amps | Set the DER to always measure low current
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
17 |  | MeasHighAmps |  |  | enum16 |  |  |  | RW |  |  | Meas High Amps | Set the DER to always measure high current
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
18 |  | MeasHighS |  |  | enum16 |  |  |  | RW |  |  | Meas High S | Set the DER to always measure high apparent power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
19 |  | MeasLowS |  |  | enum16 |  |  |  | RW |  |  | Meas Low S | Set the DER to always measure low apparent power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
20 |  | MeasHighQ |  |  | enum16 |  |  |  | RW |  |  | Meas High Q | Set the DER to always measure high reactive power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
21 |  | MeasLowQ |  |  | enum16 |  |  |  | RW |  |  | Meas Low Q | Set the DER to always measure low reactive power
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
22 |  | MeasLowPF |  |  | enum16 |  |  |  | RW |  |  | Meas Low PF | Set the DER to always measure low power factor
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
23 |  | MeasLowReversedPF |  |  | enum16 |  |  |  | RW |  |  | Meas Low Reversed PF | Set the DER to always measure low reversed power factor
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
24 |  | NameplateHighP |  |  | enum16 |  |  |  | RW |  |  | Nameplate High P | Set the DER nameplate power to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
25 |  | NameplateLowP |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low P | Set the DER nameplate power to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
26 |  | NameplateHighS |  |  | enum16 |  |  |  | RW |  |  | Nameplate High S | Set the DER nameplate apparent power to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
27 |  | NameplateLowS |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low S | Set the DER nameplate apparent power to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
28 |  | NameplateHighQ |  |  | enum16 |  |  |  | RW |  |  | Nameplate High Q | Set the DER nameplate reactive power to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
29 |  | NameplateLowQ |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low Q | Set the DER nameplate reactive power to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
30 |  | NameplateHighNomV |  |  | enum16 |  |  |  | RW |  |  | Nameplate High Nom V | Set the DER nameplate voltage to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
31 |  | NameplateLowNomV |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low Nom V | Set the DER nameplate voltage to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
32 |  | NameplateLowAmps |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low Amps | Set the DER nameplate current to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
33 |  | NameplateLowVarmaxinj |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low Varmaxinj | Set the DER nameplate VarMaxInj to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
34 |  | NameplateLowVarmaxabs |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low Varmaxabs | Set the DER nameplate VarMaxAbs to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
35 |  | NameplateLowPF |  |  | enum16 |  |  |  | RW |  |  | Nameplate Low PF | Set the DER nameplate power factor to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
36 |  | SettingsHighNomV |  |  | enum16 |  |  |  | RW |  |  | Settings High Nom V | Set the DER settings voltage to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
37 |  | SettingsLowAmps |  |  | enum16 |  |  |  | RW |  |  | Settings Low Amps | Set the DER settings current to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
38 |  | SettingsHighP |  |  | enum16 |  |  |  | RW |  |  | Settings High P | Set the DER settings power to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
39 |  | SettingsLowP |  |  | enum16 |  |  |  | RW |  |  | Settings Low P | Set the DER settings power to be low
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
40 |  | SettingsHighVAMax |  |  | enum16 |  |  |  | RW |  |  | Settings High VAMax | Set the DER settings VAMax to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
41 |  | SettingsHighVarmaxinj |  |  | enum16 |  |  |  | RW |  |  | Settings High Varmaxinj | Set the DER settings VarMaxInj to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
42 |  | SettingsHighVarmaxabs |  |  | enum16 |  |  |  | RW |  |  | Settings High Varmaxabs | Set the DER settings VarMaxAbs to be high
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
43 |  | ChangeCommonModelID |  |  | enum16 |  |  |  | RW |  |  | Change Common Model ID | Change the common model ID
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled
44 |  | ChangeCommonModelLength |  |  | enum16 |  |  |  | RW |  |  | Change Common Model Length | Change the common model length
|  | OFF | 0 | [8 empty] | Data Unaffected | Modbus Falsification Disabled
|  | ON | 1 | [8 empty] | Data Falsification | Modbus Falsification Enabled

## 64413
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | PVSimCurves |  |  | group | [6 empty] | PV Curves | Current-Voltage and Power-Voltage Profiles for PV Simulation.
0 |  | ID | 64413 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length.
2 |  | IVLen |  |  | count | [6 empty] | IV length | Number of points in the IV curve.
3 |  | Irr |  |  | uint16 |  | Irr_SF | W/m^2 |  |  | S | POA Irradiance | Plane of Array Irradiance
4 |  | Irr_SF |  |  | sunssf
IV Curve Points
|  | PVSimCurves.IV |  | IVLen | group
| 0 | P |  |  | float32 |  |  | W |  |  |  | Power | Power
| 2 | I |  |  | float32 |  |  | A |  |  |  | Current | Current
| 4 | V |  |  | float32 |  |  | V |  |  |  | Voltage | Voltage

## 64414
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | DERSimControls |  |  | group | [6 empty] | DER Simulation Controls | Configuration parameters for the DER device simulator.
0 |  | ID | 64414 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length.
2 |  | Time |  |  | string | 10 | [5 empty] | Time offset | Time offset for simulation formatted 'HH:MM:SS'
12 |  | Temperature |  |  | float32 |  |  |  | RW |  |  |  | Ambient temperature (degrees Celsius)
14 |  | GridModelSource |  |  | string | 32 |  |  | RW |  |  |  | The data source for the grid model. 'csv' or 'const'
46 |  | IrradianceModelSource |  |  | string | 32 |  |  | RW |  |  |  | The data source for the irradiance model. 'csv' or 'const'
78 |  | Irradiance |  |  | float32 |  |  |  | RW |  |  |  | The irradiance on the DER device (W/m^2) for the 'const' irradiance model
80 |  | GridVoltageA |  |  | float32 |  |  |  | RW |  |  |  | Phase A RMS Voltage (pu) for the 'const' grid model
82 |  | GridVoltageB |  |  | float32 |  |  |  | RW |  |  |  | Phase B RMS Voltage (pu) for the 'const' grid model
84 |  | GridVoltageC |  |  | float32 |  |  |  | RW |  |  |  | Phase C RMS Voltage (pu) for the 'const' grid model
86 |  | GridFrequency |  |  | float32 |  |  |  | RW |  |  |  | Grid frequency (Hz) for the 'const' grid model

## 64415
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | CSIPControl |  |  | group | [6 empty] | CSIP Client Control | CSIP Client Control for Alarms and Error tests
0 |  | ID | 64415 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length.
2 |  | LogEventEna |  |  | enum16 |  |  |  | RW |  |  | LogEvent Mode Enable | Enable or disable the LogEvent mode
|  | DISABLED | 0 | [8 empty] | Disabled | LogEvent Mode Disabled
|  | ENABLED | 1 | [8 empty] | Enabled | LogEvent Mode Enabled
3 |  | HTTPMsg |  |  | enum16 |  |  |  | RW |  |  | HTTP Message Mode Enable | Enable or disable the HTTP Message mode
|  | DISABLED | 0 | [8 empty] | Disabled | HTTP Message Mode Disabled
|  | ENABLED | 1 | [8 empty] | Enabled | HTTP Message Mode Enabled
4 |  | COMM004Cert |  |  | enum16 |  |  |  | RW |  |  | COMM-004 Certificate | Select COMM-004 certificate type
|  | Default Certificate | 0 | [8 empty] | DEFAULT | Default Certificate
|  | COMM_004A | 1 | [8 empty] | COMM-004A | Chain Length Two Certificate
|  | COMM_004B | 2 | [8 empty] | COMM-004B | Chain Length Three Certificate
|  | COMM_004C | 3 | [8 empty] | COMM-004C | Chain Length Four Certificate
|  | COMM_004D | 4 | [8 empty] | COMM-004D | Invalid MICA Extended Key Critical Value
|  | COMM_004E | 5 | [8 empty] | COMM-004E | Invalid MICA Name Non-Critical Value
|  | COMM_004F | 6 | [8 empty] | COMM-004F | Invalid MICA Policy Mapping Non-Critical Value
|  | COMM_004G | 7 | [8 empty] | COMM-004G | Self-signed device certificate